## Slide 1
DER Technical Forum
20 September 2022
13:00 – 15:00 at the ENA,
4 More London Riverside
London SE1 2AU
Microsoft Teams meeting
Join on your computer or mobile app
Click here to join the meeting
Meeting ID: 345 118 535 800 Passcode: wWcy8z
Download Teams | Join on the web
Or call in (audio only)
+44 20 3855 5885,,328234278# United Kingdom, London
Phone Conference ID: 328 234 278#

## Slide 2: Welcome, Housekeeping and Introductions

## Slide 3: Agenda
1 | 13:00 | Welcome, Introductions and Acceptance of Agenda.
2 | 13:05 | New Issues since the last forum: 125 bespoke micro generation <16A 126 SAF data for Mod Apps 127 P28 and generation trips
3 | 13:20 | Unresolved issues 112, 113, 114, 117, 121-124
4 | 13:40 | Update on BESS issues
5 | 13:55 | Update on relevant topics: G100 Fastrack GC0117 Distributed Restart EU Developments
6 | 14:10 | Type testing update: Demonstration of LFSM-O
7 | 14:25 | Current list of future G98/G99 amendments
8 | 14:35 | AOB
10 | 14:40 | Next Meeting Arrangements

## Slide 4: New Issue

## Slide 5: New Issue – 1 (125)
Q Is it allowed to connect a non-type tested PGM where the registered capacity is <16A. There are some micro-hydro PGMs below the 16A threshold, but where they are designed to meet a specific location and as such are not amenable to type testing.
A Although G99 was originally conceived as not allowing non-type-tested units of <16A to be connected, this could be overly restrictive in cases such as described. It seems that the early drafting of 2.1 in G99 was designed to accommodate this – but it is less than completely clear and is in conflict with 2.4. It is suggested that the drafting of 2.1 and 2.4 area updated as shown below.
  2.1 This EREC provides the technical requirements for the connection of Type A, Type B, Type C and Type D Power Generating Modules to the Distribution Networks of licensed DNOs in Great Britain. For the purposes of this EREC, a Power Generating Module is any source of electrical energy, irrespective of the generating technology and Power Generating Module type. This EREC applies to all Power Generating Modules which are not in the scope of EREC G98, Requirements for the connection of Fully Type Tested Micro-generators (up to and including 16 A per phase) in parallel with public Low Voltage Distribution Networks on or after 27 April 2019, or which would be in the scope of EREC G98 but are not suitable for type testing are not compatible with EREC G98.
  2.4 Specific separate requirements apply to Power Generating Facilities connected at LV comprising Fully Type Tested, Type A, Power Generating Modules 16 A/phase or less (micro-generators) and these are covered in EREC G98. All Power Generating Modules 16 A/phase or less connecting to the DNO’s Distribution Network shall be Fully Type Tested unless the DNO agrees that it is impractical where a Power Generating Module is being designed specifically for that location, such as is sometimes appropriate for micro hydro installations, etc.

## Slide 6: New Issue – 2 (126)
Q Customers are still seeing very long delays for DNOs to submit a Modification Application to National Grid for the appropriate GSP. A developer accepted a scheme Sept 2020 and only had the Mod App response back August 2022 (even with pushing for a Mod App to be done with escalation). This is not an isolated experience.
One part of the delay occurred as the DNO informed us they are allowing customers to only fill in sections 1 -3 before receiving a distribution offer, but required customers to fill in section 4 before they were able to submit the Mod App.
Whilst the customer UBGC represented had filled in Part 4 when the scheme was applied for, others which accepted before had not and a Mod App was further delayed, to allow customers who accepted ahead to fill in the form. This would have been 14+ months after they had initially accepted their offers.
If Part 4 is a requirement for a Mod App but the DNO feels comfortable making a distribution offer without part 4, can it be agreed that part 4 it is filled in within a set period, I.e. 2-3 months of acceptance to prevent further delays in Modification Applications in the future or that the Mod App is submitted based only on the information within parts 1-3.
A The timing of the provision of data is prescribed in DPC1 of the Distribution Code – needs review to see how this suggestion might be accommodated.

## Slide 7: New Issue – 3 (127)
Q
There is a requirement in ENA P28/2 (Although fairly sketchily defined) that we are supposed to consider what happens if a generator trips under full load conditions at different power factors ie 0.95 lag, unity and 0.95 lead.
We have had a fairly large number of these sites come up that have a problem on them, and when we carry out the studies, we get a fail (ie the SVC is greater than +/-3%). When we hit this point there isn’t really much we can do to help, as the SVC results are really just a function of the MW, MVAr flow and system strength – the only option is to constrain the generator MW output if it is at a problem PF – this causes headaches for developers
Some general thoughts would be
A generator tripping on full load conditions would be relatively unusual – although with G99 LoM protection I guess it can and does happen, so I can see why its there.
Is it really realistic to consider it against minimum (outage) fault condition?
Should the developer really be doing this and finding problems - it is such a simple assessment the DNO should really do this, and check before issuing an offer. In reality just a simple load flow of before and after.
A
TBC

## Slide 8: Previous Issues

## Slide 9: Outstanding Issues:
Registered Capacity – 112 – can we close this one now?
BESS connexions – issues 113, 114
Cybersecurity – 117 – to follow up with AMPS
Classification of PGMs – 121 – to follow up with AMPS
5 minutes per month for STP – 122 – can we close this one now?
G100 automatic reset for comms faults – 123 – can we close this one now?
Private wires – 124 – Can we close this one now?

## Slide 10: Outstanding Issues – 1 – can we close this one?
No | Issue | Assumed Status
112 | A common issue that keeps coming up is Registered Capacity vs design install and grid agreements. I have a specific case where the G99 and connection agreement is for 9MW, the developer undersized the inverters slightly. So it can only produce 8.5MW ( in round numbers) whilst operating in the 0.95 lag/lead range. This is what is shown when we do the G99 study, and we noted this shortfall. So the question arises, of what happens to the site now and what can it do. Specifically, 1) Is it’s new official RC 9MW or 8.5MW ie do they retain their original agreed capacity, or is this list back to the DNO? This is a common sticking point, taking the above example it cannot meet the 9MW required, but they may upgrade an inverter later to give them more MVAr headroom and it could then operate at 9MW. 2) If the DNO doesn’t want/need them to operate across the 0.95 lag/lead range can they then operate at 9MW active power and say unity or 0.98pf. In this case they are producing their official R, but their system design does not meet the required G99 standard for a 9MW site. | This is an issue that does re-appear from time to time. We have attempted to deal with it in the past in issues 40, 80 and 83. We went through it with slides at the 7 June 2022 DER TF. DNOs have summarized how they specify maximum capacities and power factors in their connexion agreements. We propose that we incorporate the material from the 7 June 2022 meeting into the next version of the DG guides

## Slide 11: Outstanding Issues – 2 – in progress
No | Issue | Assumed Status
113 | P28 has the usual classifications of frequent events, infrequent events (4 per month) and very infrequent events (1 per 3 month)…. what should we be assessing a storage system performing a dynamic containment service as? The UK grid is reasonably stable, at the moment, but with more conventional plant dropping out, the power swings are going to get a bit more sever, and the DC type services will be getting worked more often. Classing it as a very infrequent event probably isn’t realistic, but what about infrequent events? I could see that it is possible that you could get to around the 4 events per month, although probably not at the full power swing. | This is a good point, and one that probably would benefit from a consistent consideration by DNOs. It might be sensible to base the frequency on the observed incidence of frequency excursions, over the last 18 months say, that trigger a specific level of response from such services. The response level might be set locally, and the P28 “frequency of event” set by the historic track of frequency excursions triggering that level of response. This can be calculated from the information NGESO publish monthly. This should be picked up as part of ongoing work to develop a common approach to BESSs between the DNOs. However, note that in the BESS discussions on 18/11 it was pointed out that the 3% limit essentially applies at any time once the transients have died away, so for BESS power swings the 3% probably applies in all cases, irrespective of frequency of event.

## Slide 12: Outstanding Issues – 3 – in progress
No | Issue | Assumed Status
114 | We have concerns relating the voltage step change for Battery Energy Storage Systems (BESS) when the systems are designated for fast frequency response. A number of network operators define step change to be full declared export to full declared import for real power P and for reactive power Q. The FFR contracts do not have a contracted obligation to reverse the direction of reactive power flow and no obligation to match the fast MW response with a MVAr response. When importing, there is no obligation to operate at a particular power factor only to operate within a +/-0.95 range. If a full MW ramp has occurred, it is reasonable to assume the system is under stress. To reverse Q at this point would be the worst of all strategies at it would exacerbate the stress of the system by introducing an unnecessary voltage step. It is likely that EFR or FFR BESS is located at a point with a high X/R ratio (close to a BSP or GSP). Therefore a unit change in Q would have at least 10x the impact on at the voltage step that of a unit change in P. This Q reversal condition appears to be based on a false assumption about the default behaviour of inverters under FFR. We believe it is a matter for the customer to demonstrate through simulation the voltage step change under power reversal. It is a matter for the customer to produce a reactive power strategy that meets the constraints of the D Code and the connection offer. Confirmation of the simulation can be done via commissioning tests with frequency injection for smaller steps. The imposition of this requirement distorts the market by essentially limiting the capacity of a BESS scheme to around half the capacity of other technologies thus creating hidden barrier to the penetration of the technology. The customer should demonstrate how they meet the voltage step change challenge through modelling and if necessary to verify through commissioning demonstration, not for the network operator to impose a control philosophy. | To be picked up in the BESS sessions

## Slide 13: Outstanding Issues – 4 – in progress
No | Issue | Draft response
117 | Need of Effective date: Even though the current amendment is classified as minor changes there are significant changes that would require time for manufacturers to update their PGMs to comply with recent requirements. Ex one of those is the Cyber security requirement. For changes like these that would require identifying and implement a solution to an already compliant machine would take significant time/cost. Hence any requirements that would require modification of existing hardware/software design would require an effective date from the current release (a minimum of 6 months is recommended) to enable the manufacturer to be compliant with up-to-date requirements. Currently, the exception is applicable only for certain technologies but is required to be made for all technologies. Please be mindful that it would take manufacturers some time to find an effective solution and to prove compliance. | We agree that any change of requirements will generally need a period before compliance is required to allow manufacturers and others to accommodate the new requirements. As you are probably aware the recent modification to introduce new requirements for storage built in a 12 month period for manufactures and developers to implement any required changes before compliance is required. It might be that this is what you have in mind when you refer to the exception in your last sentence? We do not believe that there are any changes that we have classified as minor in the most recent amendment that impose any new compliance requirements on manufacturers or developers. Even without a specific formal implementation period, manufacturers do have significant warning of even the minor changes. They are all discussed at the DER Technical Forum, often over more than one meeting, and are summarised in the slides for the Forum which are published. The changes are formally consulted on, providing both an opportunity to absorb the proposed changes, to assimilate the implications, and provide a response or challenge to the proposals. There is then a further period, usually a couple of months, before the modification is approved by the regulator and published. In regard of the new references for cybersecurity, there is no new specific performance or compliance requirements added at this time, simply an expectation that manufacturers will be applying industry good practices, as well as standards that manufacturers should already be working to, or adapting to. It might be that the requirements of the network licensees, as provider of critical national infrastructure, do become more specific in the future, but we recognize this is a developing area and we are initially seeking to apply guidance and a light touch. In conjunction with BEIS ENA has produced guidance for Distributed energy resources (DER) cyber security connection at https://www.energynetworks.org/operating-the-networks/managing-cyber-security. However we do note your concern over the most recent change and we will be happy to discuss any points relating to them, or modifications to ENA documents more generally.

## Slide 14: Outstanding Issues – 5 – in progress
No | Issue | Draft response
121 | Minor corrections in G99 It is proposed to replace all "electricity storage devices" with "Energy storage devices". Currently, all the devices store the electricity in alternative energy form not as electric/charge form directly. Clarification on which requirements apply for Energy storage devices. As the word is included in synchronous machine and power pack modules. Synchronous machine working is limited by the machine's ability to fulfill grid codes, but convertor-based devices can be altered to fulfill stringent requirements due to electronic capability. Hence for devices that employing different technologies, it is recommended to keep the requirements separately and not to mix them. Clarity on what is the acceptable minimum level of cyber security required at the power generating module. Is it required for the power gen and the power generating control system components to be at the same security level as the facility and the ENA network? | G99 is a network oriented documented and as such it is blind to the storage medium. From the network perspective storage consumes electricity when charging, and produces electricity when discharging – ie a flow of electricity in and out. Energy storage includes heat storage, and electric vehicles, where the final output is heat and mechanical energy respectively, not electricity. The wording of the synchronous power generating module has been chosen deliberately to cater for technologies such as compressed air storage where the same synchronous machine is used for compression and expansion. In all cases the power generating module has to meet all the requirements for that technology, irrespective of how it is constituted. There are no specific requirements in G99 or G98 in relation to cybersecurity; only a general obligation to manage cyber risks appropriately.

## Slide 15: Outstanding Issues – 5 continued.
No | Issue | Draft response
121 | Gas turbine can work independent of Heat recovery system and might start working before HR blocks starts. Hence recommended to show as two different modules instead of one. As once synchronized, it is possible for GT to run independently from the HR block. Modification of synchronous power generating module definition: recommend to remove energy storage device unless it is a flywheel like device that would be used as power generating device (ex. Mechanical UPS system - rotary UPS) but these devices are least used against grid as it supports power backup for short duration and just a load on grid until the grid fails. | Figure 4.1a shows a single power generating module comprising two separate power generating units. Whilst it is true that the gas turbine unit can be run independently, it is assumed that the steam turbine cannot. If the steam turbine were capable of independent operation then there would indeed be two separate synchronous PGMs. However as the steam turbine (a) cannot run independently and (b) normally runs in tandem with the gas turbine, the two units comprise a single SPGM. As per (a) above the definition caters for technologies such as hydro pumped storage and compressed air storage. Short term energy storage devices such as flywheels, DRUPs etc are specifically excluded from G99 – see section 7.1.2: “Equipment other than Generating Units (eg traction loads, lift motors etc) may act as a short term source of energy, and inject electrical energy into the Customer’s Installation when they operate in a regenerative mode. In general EREC G99 will not apply as there will be no need to make any specific design accommodation for such equipment as it is unlikely that they will support any possible power island for a significant length of time. Where such equipment can act as a source of electrical energy for more than a few seconds (say typically 20 s), the DNO will advise the Customer if the Customer’s Installation requires any special consideration such as reverse power protection on a case by case basis.”

## Slide 16: Outstanding Issues – 7 – can we close these?
No | Issue | Assumed Status
123 | G100 Issue 2 - Communication errors: According to G.100 any communication failure, longer than 5 seconds, shall set the system to the restricted production mode and only manual intervention will enable setting the system back to the Normal operation mode. From our experience, communication error, longer than 5 seconds are not rare, and the fact that an Installer or the homeowner himself are required to be involved in this process is problematic. In order to avoid this complexity, we can offer to comply with the requirement to detect the communication failure in less than 5 second, to restrict the production to the MEL (max export limit) until the communication error is resolved, and once done to set the system automatically to its Normal operation mode. Using this approach, we will not export any current higher the configured MEL and from the other hand we will not need the Homeowner to set the system back to Normal once the problem is resolved. | This is a drafting oversight. It was always the intent right from the first discussions on the revised G100 that automatic resetting of communication errors would be allowed. G100 does not expressly forbid this, but similarly it does not say it is allowed. As this is a simple drafting oversight, the ENA will look to see how the published version can be corrected most propitiously. The proposed redrafting of 4.5.2.2 would be: 4.5.2.2 Communication Failures The Customer shall be able to reset the CLS back to normal operation immediately in every case when communication has been restored, ie the lockout feature of 4.5.1.3 does not apply. A CLS may be arranged by the Manufacturer or Installer to self-reset from state 3 when state 3 operation is caused solely by communication failures.
124 | For the situation where two existing and separate G59 generation sites A and B, supplied by the same 11kV DNO feeder, are to be connected by a private wire, leading to an increase in export capacity at site A, should the generator on site B (contributing to the increased export from site A) be made G99 compliant or not? | It is proposed to add in a new 20.3.6 to G99 to cover this. The proposed text is: In cases where an existing G59 PGM is to be connected to another customer’s installation via a private wire, the PGM does not need to be upgraded to meet G99 provided the it retains its long term parallel arrangements at its original site.

## Slide 17: Outstanding Issues – 6 – can we close this?
No | Issue | Assumed Status
122 | I represent a UK water industry working group responsible for the development and maintenance of electrical specifications. During recent work to update a specification for low voltage diesel generator sets, I was asked by the group to lobby the ENA technical committee responsible for G99 to consider relaxing the following clause in EREC G99: 7.3.3.1 parallel operation | 7.3.3.1 The Power Generating Module may be permitted to operate in parallel with the Distribution Network for no more than 5 minutes in any month, and no more frequently than once per week. If the duration of parallel connection exceeds this period, or this frequency, then the Power Generating Module shall be considered as if it is, or can be, operated in long-term parallel operation mode. An alternative frequency and duration may be agreed between the DNO and the Generator taking account of particular site circumstances and Power Generating Module design. An electrical time interlock should be installed to ensure that the period of parallel operation does not exceed the agreed period. The timer should be a separate device from the changeover control system such that failure of the auto changeover system will not prevent the parallel being broken. Notice that the highlighted text already allows for an agreement between the DNO and Generator to agree an appropriate testing regime, subject to there being a valid reason to do so. An alternative would be to fit full LoM protection and address any relevant points from 7.3.3.4, in which case the PGM would be treated as LTP. To be reviewed as part of the next update to G99.

## Slide 18: Battery Energy Storage Systems

## Slide 19: BESS discussion session
A session with stakeholders was held on 13 April 2022.
  The revised Standard Application Form reflecting the agreed changes to the questions about reactive power flow requirements was published on 28 April.
  DNOs are still considering other challenges of voltage management, including the effect of multiple BESSs in the same are, and the effects on other customers.
Another follow up meeting has been arranged for 05 October 2022.

## Slide 20: Summary of DNOs’ BESS P28 policies – Planning Criteria*
 | Single Installation |  |  | Co-incident swing |  | 
DNO | pf | Contin-gency | Voltage Step change | Contin-gency | Voltage Step change | Location considered/Comments
WPD | 0.95 lead when exporting; 1.0 when importing | n-1 | 3% | n-1 | 6% | Connection Point and busbar of source substation (ie primary, BSP or GSP)
UKPN | 1 | Initially system Intact | 3% | System Intact | 3% | Connection Point - In all cases the voltage step change is monitored at the Connection Point and any substation busbars where it’s considered the BESS will have a material effect. If the step change assessment results are not satisfactory (also applies to single installations), then a more specific power factor range is defined and included in the Connection Agreement. The coincident swing covers all BESS (HV, EHV & 132kV) on a GSP and the voltage step change is monitored at all substation busbars (primary, BSP & GSP) under that GSP.
SPEN SPD | 0.95 lead when exporting; 0.95 lag when importing | n-1 | 3% | n-1 | 3% | Connection Point and source GSP including all Primary substations – Voltage step change is monitored at GSP and any Primary substation busbars where BESS will have an effect (GSP busbars and Primary substations connected at that GSP).
SPEN SPM | 0.95 lead when exporting; 1.0 when importing |  |  |  |  | 
*Used for initial assessment, as opposed to agreed operating requirements

## Slide 21: Summary of DNOs’ BESS P28 policies – Planning Criteria* - 2
 | Single Installation |  |  | Co-incident swing |  | 
DNO | pf | Contin-gency | Voltage Step change | Contin-gency | Voltage Step change | Location considered/Comments
NPG | 0.95 lagging (When exporting real and reactive power) 0.95 lagging (when importing real and reactive power) | n-1 | 3% | n-1 | 3% | Point of common coupling / Point of Supply Comments: 0.95 power factor is our initial modelling parameter for connection studies unless the customer has specified any specific power factor value. If customer requests, we will consider closer to unity power factor to reduce the voltage step change subject to NGET requirement for VARs compensation. This will be referenced in the connection agreement but Northern Powergrid reserves the right to alter the agreed operating power factor on a later date to meet the network conditions if required Northern Powergrid public policies here: LV; HV; EHV; 132kV
ENW | 1 | n-1 | 3% | n-1 | 6% | Assume 0.95 pf lead on export, unity on import. We believe operation in voltage control mode has potential to mitigate voltage step change and are now looking closely at this.
*Used for initial assessment, as opposed to agreed operating requirements

## Slide 22: Update on G100 and Fast Track

## Slide 23: G100 & Fast track
G100
  Issue 2 Amendment 1 has been published on 25 July.
  There are a small number of other points that stakeholders have commented on that would benefit from review at a suitable future time.
Fast track
  Ofgem has approved the modification on 09 September – effective from 09 November.

## Slide 24: GC0117

## Slide 25: Grid Code Modification Proposal GC0117
Objective is to align the definition of Small and Large across GB.
NGESO’s proposal is to lower the Large threshold to 10MW in England and Wales.
Several alternative proposals were being considered:
    Implement the 50MW-100MW Medium classification in Scotland
    Raise the 10MW and 30MW threshold in Scotland to 100MW
    Implement 50-100MW Medium in Scotland, but add in some balancing mechanism requirements to all generation in this range in GB – and move the 50MW to 10MW.
    As 3, but with all generation from 1MW and above having to agree to be part of a Regional Development Programme

## Slide 26: GC0117 – alignment of Large, Medium and Small across GB
The WG consultation closed on 05 August:
  Out of 14 respondents, 3 support the original proposal and 3 support the WAGCM1 proposal. With some expressing that the solutions had not been fully developed. Others believe that a CBA and further investigations are required to fully assess the proposed solutions against the applicable Grid Code objectives.
  Some respondents expressed that the rationale / case for change is not clear. No demonstration of how the change would simplify and align Grid Code and generation considering discrepancies identified.
  Majority of respondents agreed that it is appropriate to change the definition of Demand Capacity and associated Grid Code definitions to align with the changes to Large, Medium and Small Power Stations but, via a separate modification.
  Most respondents were in support of revising the definition of Registered Capacity.
  Most respondents do not support a retrospective approach as it will be complex and result in increased costs.
  Majority supported establishing a holistic view of the required future net zero arrangements of the technical and commercial arrangements for connecting new and operating existing and new generators.
  A respondent advised that a holistic review is already being taken forward by the Open Networks project and continuing with GC0117 could result in duplication of effort and recommendations contrary to proposals under Open Networks.
There are now 3 formal proposal – the original and two WAGCMs.
  The original proposes the Large threshold at 10MW;
  WAGCM1 proposes extending the current E&W regime to Scotland;
  WAGCM2 proposes a variation on LEEMPS, but with a Medium threshold of 10MW.
The next WG meeting is 25 October.

## Slide 27: Distributed ReStart: GC0156 Electricity System Restoration Standard

## Slide 28: Electricity System Restoration Standard – GC0156
Distributed Restart is now being progressed as part of the wider ESRS implementation in GC0156.
GC0156 has a significant number of issues to understand and resolve, and an ambitious timeline.
It seems likely that the implications for DNOs will revolve mainly round Distributed ReStart – although the extent and possible mandatory nature of some of the obligations on DNOs are still emerging.
GC0156 will provide opportunities for embedded generation to seek contracts with NGESO and the DNO for system restoration.
Note that GC0148 (forerunner of GC0156) is proposing to make emergency frequency response mandatory for all storage caught by the Grid Code. The expectation is that the Distribution Code will follow suit in due course, probably during 2023.

## Slide 29: EU Developments

## Slide 30: EU Update
Not much to report since our last meeting – Europe has been on a long summer holiday.
There remains the possibility that EN 50549-10 will be published at the end of 2022 – although another review iteration might happen – in which case it would be probably 12-18 months later.
ACER is working on a public process to suggest revised EN Network Code for grid connexion by the end of 2023.
There are three current expert groups - which may or may not feed into ACER’s work, dependent on timing:
  Harmonization of Certification and Produce Family Grouping
  Grids with a high penetration of PPMs
  Offshore grids
The first two of these might have some effect on the European Market and standards – but they are still in very early stages.

## Slide 31: LFSM-O reminder of compliance requirements

## Slide 32: Assessment of Droop – particularly for Type Tested generating units
The assessment of the LFSM-O droop (for Type A) is undertaken from a couple of steps in frequency:
And droop is the marginal change in frequency for the marginal change in power output.
In GB, the marginal change in power output is defined as being the change in power cf the registered capacity, whereas in most of the rest of the world is the change in power cf the instantaneous power.

## Slide 33: LFSM-O compliance for Power Park Modules
LFSM-O droop definition is the responsibility of NGESO.
NGESO have defined this in two ways – (a) as a droop between 2% and 10%, and (b) “at a minimum rate of 2% of output per 0.1 Hz deviation of system frequency above 50.4 Hz” which equates to 10%.
The complication arises because the reference power output for droop is commonly taken to be the instantaneous active power output – this is the definition of droop used universally in Europe and is also used in 50549 and 50438.
However, NGESO have defined the reference power output as Registered Capacity – which is their right under the law – but it puts GB at odds with manufacturers’ expectations.
LFSM-O, with a droop of 10% (which is a minimum performance requirement), is actually quite hard to test for in very small generating units (ie G98 size units etc), with errors on the measurement risking obscuring the actual droop.
Testing from full output, the instantaneous active power output is the same as the Registered Capacity – so there is no issue with the results.
However, when testing from, say 50% of RC, the droop will appear to be twice what it should be if the incorrect assumption about the reference power output is made.

## Slide 34: LFSM-O compliance for Power Park Modules – 2
Although the droop is potentially twice what it should be, it is not particularly obvious because of the difficult in measuring accurately the effect of droop at 10% (ie it is much more obvious at a lower droop, say 4%).
Some manufacturers persist in supply droop based on instantaneous power, rather than Registered Capacity.
G98 and G99 would benefit from a small amendment to make the GB requirements much more prominent – but in the mean time it would be good to bring this to manufacturers’ attention generally.

## Slide 35: Current list of G98/G99 potential updates – see appendix

## Slide 36: AOB and next meeting
AOB
None?
Next meeting?

## Slide 37: Appendix - Current list of future G98/G99 amendments

## Slide 38: G98/G99 list of outstanding modifications April 2022 - significant
# | Date raised | Raised by | G98/G99 reference | Discussion | Specific modification
1 | 10/02/21 | AC | G99 6.3.7 | Need to be more specific about which models are being referred to. In G99 reference is made to ‘detailed models’, ‘simulation models’ and ‘control system and prime mover models’. There may be merit in trying to add further clarity of the different models required for PGMs and which need to be verified. | In general detailed models of a Type A or Type B Power Generating Module are not required. Where the DNO deems it necessary to ensure System Stability and security appropriately detailed models of Type A or Type B Power Generating Modules and their control systems shall be supplied. Detailed models are always required for Type C and Type D Power Generating Modules. Generators shall submit detailed models in respect of Generating Units which are aggregated into a Power Park Module.
2 | 22/03/21 | AH | G98 forms | Form D, Decommissioning: “I enclose a copy of the system schematic which has been left on site at the Customer’s incoming meter location.” This requirement should also be in Form B, Installation document | I declare that the relevant Micro-generators and the installation which together form a Micro-generating Plant within the scope of EREC G98 at the above address, conform to the requirements of EREC G98. This declaration of compliance is confined to Micro-generating Plant tested to EREC G98 or EREC G83 as applicable at the time of commissioning. I enclose a copy of the system schematic which has been left on site at the Customer’s incoming meter location.
3 | 31/01/21 | AH | G99 Form C3 Part Installation and Commissioning Confirmation Form for Type C and Type D PGMs | Check proposed that the Dynamic System Monitoring & Fault Recorders and PQ monitoring equipment has been commissioned (Type C&D) | 

## Slide 39: G98/G99 list of outstanding modifications April 2022 - significant
# | Date raised | Raised by | G98/G99 reference | Discussion | Specific modification
4 | 07/06/21 | DER Tech forum #101 | G99 C.7.6 | Following discussion with National Grid it is recognised that the studies requested in G99 are appropriate if the Generator is intending to operate the PGM in island mode, otherwise the standard ramp response simulations as for Type B are sufficient for distribution connected plant. | Clarification to be added to C.7.6
5 | 10/11/21 | DNO SG | G98, G99 and SAF data requirements | Energy conversation technology tables - rows 30-32 are not electricity storage – they should not be in this list Need to align with DUCSA mods and NG | Remove rows 30-32
6 | 10/12/21 | AC |  | Amend G98 to allow devices suitable for island mode operation eg storage & PV combination, so that a house could operate in island mode ‘easily’ in the event of an extended power outage. G98 points to G99 for island mode – which allows it if it’s appropriately designed | In progress
7 | 14/01/22 | MK/LB | G98 Additional clause | Small (G98) PV installation where the DNO connection is HV metered. Should it be accepted by DNO as G98 notification only or go through G99 simple less than 50kW route? | New 2.18 The approach detailed in this EREC G98 should be used for a single Fully Type Tested Micro-generator connecting to a Customer Installation at LV, where the customer is supplied at HV and where there is no other generation.

## Slide 40: G98/G99 list of outstanding modifications April 2022 - significant
# | Date raised | Raised by | G98/G99 reference | Discussion | Specific modification
8a | 31/01/22 | MK | G99 2.15 | Clarity of validity of type tests needed | 2.15 Validity of Type Tests 2.15.1 Power Generating Modules that have been Type Tested to demonstrate compliance with previous amendments of EREC G99, and already connected to the Customer’s Installation, remain valid for this current version of EREC G99. Where compliance of an item of plant and/or apparatus is demonstrated using Manufacturers’ Information or Equipment Certificate(s) the compliance should be with the version of this EREC G99 that is current at the time of acceptance of the connection offer, or with any later version of this EREC G99. 2.15.2 Where a new amendment to EREC G99 changes a requirement which a Manufacturer has previously certified as compliant, that certification becomes invalid from the date that the revised requirement in the new amendment becomes operative. Manufacturers will need to submit updated certifications for EREC G99 compliance for any relevant Power Generating Module which is connected on or after the date the revised requirement becomes operative. 2.15.3 For Type Tested Power Generating Modules, the relevant requirements are those that are principally laid out in sections 9 to 14 of this EREC G99 and which are generally expected to be demonstrated in accordance with the provisions of sections 15 to 19 of EREC G99. Minor updates to EREC G99 which are clarifications and do not change the underlying requirements are not classed as changed requirements and therefore do not need Manufacturers to repeat tests and re-certify.

## Slide 41: G98/G99 list of outstanding modifications April 2022 - significant
# | Date raised | Raised by | G98/G99 reference | Discussion | Specific modification
8b | 31/01/22 | MK | G98 2.15 | Clarity of validity of type tests needed | 2.17 Micro-generators that have been Fully Type Tested to demonstrate compliance with previous amendments of EREC G98 and are already connected to the Customer’s Installation, remain valid for this current version of EREC G98. 2.18 Where a new amendment to EREC G98 changes a requirement which invalidates a Micro-generator’s Fully Type Tested status, that certification becomes invalid from the date that the revised requirement in the new amendment becomes operative. Manufacturers will need to submit updated certifications for Fully Type Tested status for any Micro-generator which is connected on or after the date the revised requirement becomes operative. 2.19 The relevant requirements are those that are principally laid out in sections 9 to 11 of this EREC G98 and which are generally expected to be demonstrated in accordance with the provisions annexes A1 or A2 of EREC G98. Minor updates to EREC G98 which are clarifications and do not change the underlying requirements are not classed as changed requirements and therefore do not need Manufacturers to repeat tests and re-certify.
9 | 16/02/22 | MK | G99 | G100 Type test device might be incorporated into G99 equipment. Consider allowing this to be noted on G99 forms | Opportunity on forms to check that there is an export limiting device that is integral to this G99 device for which the G100 type test form will also be submitted. Reference of G100 form.

## Slide 42: G98/G99 list of outstanding modifications April 2022 - significant
# | Date raised | Raised by | G98/G99 reference | Discussion | Specific modification
10 | Current | MK/SC | G98 & G99 | GC0148 outcome Storage response to rising freq after a fall (System recovery) | Refer to NG words once finalised. Currently draft (15/02/22) on GC0148 website.
11 | 21/04/22 | LF | G99 Form A2-3 | Different approach between G98 and G99 wrt requirement for evidence for output power with falling frequency (G98 Form C). Should output power with falling frequency be in G98 Form A1? It is appropriate in A2 – as this is a rotating machine phenomenon. Don’t think a BESS manufacturer should be looking at A.7.2.3 in G99 as this is for rotating machines. And which is why it’s not in A2-3. | Remove requirement from A1 Check consistency in G99
12 | 21/4/22 | SG | G99 | Usually prototypes do not have any pre-certificate or compliance report to connect to the grid. Currently a derogation is required for such builds to connect to grid as they don’t fulfil G99 requirements and require testing to be done against grid to obtain certification. Can an allowance be made for the connection of prototypes as in the VDE4110 2018 standard | To be developed following agreement in principal by DNOs
13 | 05/07/22 | MK/DNOs | G99 | Compliance of exisiting generators involved in private wire schemes see 07 July 2022 DNO mtg ppt for discussion | New 20.3.6 (and renumber the existing as 20.3.7) In cases where an existing G59 PGM is to be connected to another customer’s installation via a private wire, the PGM does not need to be upgraded to meet G99 provided the it retains its long term parallel arrangements at its original site.

## Slide 43: G98/G99 list of outstanding modifications April 2022 - significant
# | Date raised | Raised by | G98/G99 reference | Discussion | Specific modification
14 | 05/07/22 | DNO EU Code mtg | General And G83 | EU housekeeping modifications | See mods approved by Ofgem, e-mail CMC 04/07/22
15 | 06/07/22 | SS/MK | FFCI | The wording is ambiguous in the Appendices (B.4 and C.7) compared to the main body of the text. GC0155 mod FFCI is required for all faults, not just symmetrical | Refer to GCode text following GC0155 conclusion
16 | 31/8/22 | Eckhard Schwendemann | G99 11.2.4 LFSM-O | Clarity required in respect of 11.2.4.1.(c) and 11.2.4.1(d). A7.9 demonstrates what is expected for 11.2.4.1.(d) and A7.10 demonstrates what is expected for 11.2.4.1(c). A7.9 demonstrates that the response should be at 0.5% per second, and allows for a 2s delay in the response starting. A7.10 shows that for excursions above 50.4 the response must achieve half the required reduction within 10s, again allowing for a 2s delay. I think it is implicit that after 10s the reduction should be linear – it’s obvious from the graphs – but I suspect it might be useful to make it explicit in 11.2.4.1(c). | Modify text of 11.2.4 to refer to figures A.7.9 and A.7.10
17 | 31/8/22 | Eckhard Schwendemann |  | A.7.3.1 Domestic CHP and A.7.3.3 Fuel Cell. Consideration of the dynamic characteristics of the SOFC (high temperature fuel cell) Technology which can offer modified dynamic requirements in the area of change of active power to lower gradients. | 

## Slide 44: G98/G99 list of outstanding modifications April 2022 – minor editorial
# | Date raised | Raised by | G98/G99 reference | Discussion | Specific modification
1 | 14/10/21 | SC | C.6.3 | Mod ref to G5/4 in C.6.3 to just G5 | 
2 | 14/10/21 | SC | G99 21.4 | 21.4 …..The DNO will consider the suitability of Manufacturers’ Information in place of DDRC data submissions such as a mathematical model suitable for representation of the entire Power Park Module as per Annex B.4.4 or Annex C.7.4.5 as applicable. Site specific parameters will still need to be submitted by the Generator. References to Annexes need correcting | 21.4 …..The DNO will consider the suitability of Manufacturers’ Information in place of DDRC data submissions such as a mathematical model suitable for representation of the entire Power Park Module as per Annex B.4.4.5, Annex C.7.4.5, or Annex C.7.5.5 as applicable. Site specific parameters will still need to be submitted by the Generator.
3 | 3/11/21 | MK | G99 figures 12.7 | Graphs detached from captions | Formatting
4 | 24/11/21 | AC | G98 Form B G99: Form A3-1 Form A3-2 Form B2-1 Form B3 Form C2-1 Form C3 | Use of technology type | G98 Form B Use a separate line for new and existing installations and for each micro-generator . G99 Modify forms in line with Form A-1-2 Energy source and energy conversion technology (enter codes from tables 1 and 2 see Form A1-2)

## Slide 45: G98/G99 list of outstanding modifications April 2022 – minor editorial
# | Date raised | Raised by | G98/G99 reference | Discussion | Specific modification
5 | 1/02/22 | VH | G99 Annex A.6 | This table is applicable to all Generator Types, not just type A | Could move to Annex D, or ensure it is clear that this table is also applicable to Types B, C &D
6 | 29/03/22 | MK | G99 A.7.2.1 | Storage words should be removed in line with removal of storage exclusions | Remove: A.7.2.1 This Annex also applies to any Synchronous Power Generating Modules that are powered by stored energy (eg compressed air), but the requirement to demonstrate the LFSM-O will not be required.
7 | 04/05/22 | AC | G99 11.1.1, 12.1.1 and 13.1.1 | G99 A.4.3 states that for ‘infrequent short-term parallel operation’ for a Type X PGMD, then none of Section Y applies. E.g G99 13.1.1 (a) states that the ’requirements of this Section 13 do not apply in full’, implying that some parts of section 13 apply, which doesn’t align with the statement in A.4.3. | Check which way to go- exclude everything in S 11,12 13 or use storage derogations….
8 | 23/06/22 | SC | G98 A .1.3.2 | Reference to “full load” should be Registered Capacity | The test set up shall be such that the Inverter supplies full load Registered Capacity to the DNO’s Distribution Network via the power factor (pf) meter

## Slide 46: G98/G99 list of outstanding modifications April 2022 – minor editorial
# | Date raised | Raised by | G98/G99 reference | Discussion | Specific modification
9 | 28/06/22 | LF | G99 A2-3 | Does not have Output power on falling frequency tests | See Forms A2-1 or Form C in G98. Check Annex Ensure alignment with storage operating mode switch
10 | 30/06/22 | Emanuelle Lelli Aton Storage | G99 | E-mail from 30/6/22 Muddle in G98/G99 re source impedance | Modify note : Applies to three phase Micro-generators and two phase Micro-generators in split phase system Similar for G99
11 | 09/08/22 | SC | G99 A.7.2.5.1 | Ref to export capacity should be RC | The tests should be carried out as specified in BS EN 61000-3-12 and can be undertaken with a fixed source of energy at two power levels firstly between 45 and 55% and at 100% of maximum export capacity. Note that if the suggested output level is below the Power Generating Module’s Minimum Stable Operating Level the test should be carried out at 100%, and at least one stable output level below 100%, of Registered Capacity. It is recommended that an output level is chosen that is 5% of the difference between the Registered Capacity and the Minimum Stable Operating Level above the Minimum Stable Operating Level:
12 | 31/8/22 | Eckhard Schwendemann | G99 A.7.2.5.1 | In correct reference to paragraphs wrt A.7.1.3 and A.7.2.4.2 | A7.1.3 The frequency at each step should be maintained for at least one minute as illustrated in figure A.7.3 and the Active Power reduction in the form of a gradient determined and assessed for compliance with paragraph 11.2.4. A.7.2.4.2 This paragraph is applicable to all Synchronous Power Generating Modules other than slow acting micro hydro Synchronous Power Generating Modules which should refer to paragraph A.7.2.5.2.

## Slide 47: D Code modifications April 2022
# | Date raised | Raised by | D Code | Discussion | Specific modification
1 | 25/01/22 | MK/CMC | DDRC | SAF Amendments for BESS should be added to DDRC | 
2 | 14/04/22 | AH/MK | G100 and DPC6.7.8 – Access to DNOs’ Current and Voltage Signals |  | 
3 |  |  |  |  | 
4 |  |  |  |  | 

## Slide 48: Others points
Distributed restart project mods
EU developments
GC117 LMS

## Slide 49: EN50549-10 Requirements for generating plants to be connected in parallel with distribution networks - Part 10: Tests for conformity assessment of generating units
Initial consideration of draft standard against G98 testing requirements (mainly Annex A) for PPMs
G98 (order follows Form C type test verification report) | EN50549-10
A.1.2.10 Operating range – tests at different voltages, frequencies and unity power factor for different periods of time & RoCoF immunity | 5.2.1 Frequency operating range, 5.2.2 Voltage operating range, 5.3.1 RoCoF immunity We align with stringent requirements However durations are not as onerous as standard (this has been queried)
A.1.3.1 PQ Harmonics – BSEN 61000-3-2 “Old” drafting re group testing for < 2kW units | 5.7 EMC Ref to BS EN 61000-3-2, 40th harmonic Group tests not considered, but probably OK as most installations will be now be at least 3.6 kW.
A.1.3.3 PQ Voltage fluctuations and Flicker “Old” drafting re group testing for < 2kW units | 5.7 EMC Ref to BS EN 61000-3-3 Group tests not considered, but probably OK as most installations will be now be at least 3.6 kW

## Slide 50: EN50549-10 Requirements for generating plants to be connected in parallel with distribution networks - Part 10: Tests for conformity assessment of generating units
G98 | EN50549-10
A.1.3.4 PQ DC injection | 5.7 EMC 3 levels of power 30-40%, 60-70% and > 95% which are different to G98. EN61000-4-7 is referenced wrt measurement periods. Group testing not mentioned, probably OK
A.1.3.2 Power factor 3 test V, -6%, nominal, +10% | Refs 5.5.1.3 Verification procedure to determine the power capability (active, reactive, apparent) at nominal voltage 5.5.1.6 Verification procedure for reactive power capability considering voltage range Reactive power capability is determined at different power levels and ±10% Voltage
Protection – frequency and voltage A.1.2.2 & A.1.2.3 | 5.8 Interface protection Considers both voltage and frequency protection. Considers Ramp tests (similar to G99) to verify the setting values, Jump tests to check durations (operating times time delays etc) and Non- operation signal tests

## Slide 51: EN50549-10 Requirements for generating plants to be connected in parallel with distribution networks - Part 10: Tests for conformity assessment of generating units
LFSM-O GB requirements |  | 
Frequency threshold fth (Hz) | 50.4 | 50.4
Droop (%) | 10 | 10
Power level at start of test (%Pn) | > 80% | 40-60%
Intentional delay (s) | 0 | 0
Configured deactivation threshold and time fstop (Hz) / tstop (s) |  | 
G98 | EN50549-10
A.1.2.4 Protection – loss of mains | 5.8.6 Islanding Detection Passive and active anti islanding detection considered, EN62116 referenced
A.1.2.6 Protection – vector shift | 5.3.2 Phase jump Test details given. No requirements yet in EN50549-1
A.1.2.6 Protection – RoCoF stability | 5.8.3.4 ROCOF protection Test details given, above and below setting, positive and negative
A.1.2.8 LFSM-O | 5.4.3.2. Power response to over-frequency DSO can specify frequency threshold and droop setting. Table 6 has some default values. We could replicate Table 6 with GB values Tolerances and accuracy (specified in EN50549-1) align with G98 We could continue to detail the resulting overall tolerance

## Slide 52: EN50549-10 Requirements for generating plants to be connected in parallel with distribution networks - Part 10: Tests for conformity assessment of generating units
G98 | EN50549-10
A.1.2.7 LFSM-U | 5.2.1 Frequency operating range When evaluating the underfrequency condition the generating unit is allowed to decrease its power output up to 10 % Pmax per Hertz starting from 49.5 Hz according to characteristic described in EN 50549-1:2019 and EN 50549-2:2019, 4.4.3, Figure 5 or to a more stringent power reduction characteristic defined by the manufacturer or responsible party or a specific grid code. We will need to specify as we have more stringent requirement than default 10% allowed. Maximum allowed ∆P/Pm = 5%, when f = 47.5 Hz starting from 49.5 Hz.
A.1.2.8 Storage response | 5.4.3.3 Power response to under-frequency Figure 22 is specifically for storage which is initially charging. The default power level is -50% Pn, but DNO can specify other settings

## Slide 53: EN50549-10 Requirements for generating plants to be connected in parallel with distribution networks - Part 10: Tests for conformity assessment of generating units
G98 | EN50549-10
A.1.2.5 Reconnection Minimum time delay 20 s | 5.9 Connection and starting Table 32 - Default parameter automatic reconnection after tripping according to EN 50549-1:2019 and EN 50549-2:2019 Default setting is 60 s observation time, range is 20 s – 600 s. We could specify check that minimum time is 20 s. 5.9.3 Automatic reconnection after tripping 5.9.3.1 Verification procedure Specifies the tests
A.1.3.5 Short Circuit Current Contribution for Inverters | 5.3.3 Fault ride through, over-voltage (OVRT) and under-voltage (UVRT) When required by the applied grid code or requirement document, this test procedure is also intended to provide evidence of controlled short circuit current contribution. Test procedure and recording detailed

## Slide 54: EN50549-10 Requirements for generating plants to be connected in parallel with distribution networks - Part 10: Tests for conformity assessment of generating units
G98 | EN50549-10
Logic Interface | 4.2.9 Test by changing a control parameter More complex than need for G98 – but flexible and a Conformity assessment is undertaken to enable a statement of conformity to be issued.
A 1.3.6 Self-Monitoring - Solid State Disconnection | Solid state switching not specifically covered, however consideration of failure around the interface switch is.
Cyber security | Not covered

## Slide 55: EN50549-10 Requirements for generating plants to be connected in parallel with distribution networks - Part 10: Tests for conformity assessment of generating units
Conclusions:
EN50549-10 contains an apparently comprehensive, detailed set of tests for LV/MV generators
It is possible to specify values to be used in some of the tests as appropriate
Detailed tests for other technical requirements – Type B – not yet reviewed
Once the standard is formally adopted we should consider revising G98 and G99 to reference it (and EN50549 part 1 & 2) and hence remove some of the detail of requirements and testing in G98 and G99

## Slide 56
© ENA 2020