## Slide 1: DER Technical Forum
DER Technical Forum
21 April 2020
10:30 by Webex
Webex hyperlink
Join by telephone 0203 478 5289
Meeting number (access code): 847 197 227

## Slide 2: Welcome, Housekeeping, Introductions

## Slide 3: Agenda
Time | Focus | Leader
1030 | Welcome, Introductions and Acceptance of Agenda. | MK/MD
1035 | Acceptance of minutes of previous meeting (26 February 2020) | MK
1040 | Matters arising not covered by the agenda None | 
1040 | New issues raised since the last meeting: None | 
1045 | Follow up issues from previous meeting 77 90 95 96, 97 61, 79, 93, 94 – hold over to H2 2020 | MK/TM AH MK/SC MK
1130 | Agree to close the following issues: 76 87 88 98 | MK
1135 | ENA Database update | MD
1145 | Other updates | MK
1150 | AOB | 
1200 | Meeting Close – Discuss when to hold future meeting | All
 | Meetings in 2020: TBA | 

## Slide 4: Minutes of previous meeting and actions
Accept, together with slides and running list of issues, as correct record of the meeting.
Matters arising not on the agenda:
  None

## Slide 5: Unresolved Previous Issues – 1
No | Issue | Assumed Status
77 | In sections C.6.2.5.1 (a), (b), (c) and Sections C.6.2.5.2 (a), (b) there is a requirement for the Recording Device to record and set a trigger for a configured Step % and Phase Step °. Where units support RoC and under/over/deviation in frequency, voltage and current, is Step % and Phase Step ° an essential requirement? | What is meant by “step %” and “phase step °”? The ‘step (%)’ trigger in Table C.6.2 would start a dynamic system event half-cycle trigger on a value jump of the specified value. The ‘phase step (°)’ trigger in Table C.6.2 would start a dynamic system event half-cycle trigger on a phase jump of the sine wave zero crossing of the specified value. The ‘step (%)’ trigger in Table C.6.4 would start a fault recorder event half-cycle trigger on a value jump of the specified value. The ‘phase step (°)’ trigger in Table C.6.4 would start a fault recorder event half-cycle trigger on a phase jump of the sine wave zero crossing of the specified value. The text and tables in EREC G99 set out the requirements for triggering. The requirements for specific triggers are defined. The precise specification of the triggers is beyond the scope of the document but note that BS EN 61000-4-30 Class A is specified in the text as a requirement. Note that this standard does include a definition of a term that could be used in association with step (%) term called ΔUss. The phase step is not defined although phase shift in the context of voltage dips does appear in the informative annex. Following further discussions with Siemens it is now proposed to discuss the requirements of C.6 again with NGESO and to modify C.6 formally: Remove frequency step as a current mandatory requirement, but retain it as an optional requirement that maybe reinstated as mandatory in the future; Remove current step change Agree to a different or stepped accuracy requirement for reactive power Review again the needs for timing accuracy and resolution given the likely future needs for resolution of vector shift etc. The above issues have largely been resolved. It is proposed to publish an informal consultation in Spring 2020 proposing how all these issues should be addressed, targeted at the manufacturers of these devices. Formal amendment to G99 to follow in due course.

## Slide 6: Unresolved Previous Issues – 2
No | Issue | Assumed Status
90 | We are finding the G100 requirements restrictive as our engines are starting and stopping 4-5 times a day as we cannot respond quick enough to changes in load so tripping the G100 reverse power relay. This obviously puts mechanical strain on our engines but also makes the network less stable by tripping our engines. Would it be possible to discuss extending the maximum time the reverse power relay responds from 5 to 30 seconds? | The DNOs are investigating how flexibly G100 can be interpreted/implemented
95 | Figure C.5.2 has the areas defined by AHG and DCE shaded in blue to indicate that reactive capability is not required in these regions. Could you confirm that the same principle applies to Figure C.5.2. and Figure 13.11? | Figure C.5.3 has blue shading to differentiate it from Figure C.5.2 as the latter is for voltages above 33kV and the former is for voltages of 33kV and below – corresponding to the requirements of 13.5.4 and 13.5.5 respectively. C.5.3 is drawn with the shading as the reactive capability requirements are not required in the shaded area (figure 13.2). This point would probably be less confusing if the graphs were drawn with voltage as abscissa, but the format is long standing in the GB Grid Code. Confirmation has been obtained from NG that whilst the plant connected at voltages > 33kV does not have to be capable for providing full reactive capability outside the voltage range of ±5% it should remain connected and provide as much reactive capability as possible (figure 13.11). Point D is variable by design, being dependent upon the technology used. G99 C.5.3.7 covers lines DE and AH in the diagram and states that they are “examples of the capability”. We are not proposing any changes to G99.

## Slide 7: Unresolved Previous Issues – 3
No | Issue | Assumed Status
96 | Review/revise the test requirements for constant output with falling frequency for Type B | This issue needs more discussion. It is an area where G99 expects some discretion, the PGMD allows MI and TV at the IS stage and then extends this to T at the FON stage which could be reviewed. The phrasing in B5.3 is “can”, not “shall”. We agree that control action is a key aspect to prove and that in some cases there will only be the inherent capability of the machine – so no control action to test. Our thinking on this so far has been guided by the draft EN 50549 part 10 and by pre-existing requirements for smaller type tested units. This particular issue is being pursued in discussions between Qmulus and WPD. If there are any general principles arising from the discussion they will be brought back to the forum.
97 | Discuss the use of ION for Types A B and C power generating modules | Arguably we have already dealt with this in Issues 19 and 50. All DNOs subscribe to the approach of G99 17.4.2 – ie for Type B and C generating modules DNOs will agree a period of time within which final testing and submission of data can be accomplished. The default periods are 28 days for synchronous plant, and 6 months for power park modules, recognizing the seasonal availability of some renewable resources. Of course if synchronous plant is driven by renewable resources then a period longer than 28 days might well be initially agreed. The 28 day or 6 month period is just one of expectation within which most distribution projects will be complete. As such it is just a prompt for a discussion between the DNO and the developer to reconfirm appropriate progress etc and agree future milestones with the DNO. There is no intention by the DNOs to take any sort of enforcement actions whilst the Generator is clearly still engaged in the overall commissioning programme and can show how progress towards ultimate completion of the compliance tests is to be achieved.

## Slide 8: Issues for H2 2020 - 1
No | Issue | Assumed Status
61 | 21.1.1: “Manufacturers’ Information covers such information as type testing details, parameters or data, simulation models and reports on studies run using those models.” If so, then all the forms (e.g. B2-1) that contain both MI and TV should include either MI or TV, but not both because it can be confusing. As a general comment, such forms, albeit useful, make it very hard to properly define our scope for each project; how should we interpret the “key to submission stage” in conjunction with the “key to the evidence requested”? For instance, interface protection on page 282: which of the MI, TV, T items are requested at IS and which are requested at FONS stage? Are all are all of MI, TV, T items needed or some of them or only one of them or a particular combination of them? | DNOs are not specifying how the Generator (and manufacturer) will prove compliance - that is the Generator’s responsibility. All we are doing here is setting the DNOs’ expectations as to what are the possible sources of confirmation of compliance – hence the title for the fourth column in B2-1 includes “(and / or)” to signify the choices that the Generator can make in selecting how compliance is demonstrated. This column is really for guidance and helping the Generator to explain what information he is submitting. Technical Forum is considering how/if this might be improved.
79 | Customer has identified that only certain tests in the A2-1, A2-2 have an asterisk and as such are the only tests that may be carried out at time of commissioning. Their argument was that at least for synchronous machines some of the other tests can also be undertaken on site | There could be some minor inconsistencies. Anything in theory can be demonstrated on site, save for operating range for asynchronous and fault ride through for both. LFSM-O might be hard for some units too depending on the availability of the ability to simulate frequency changes. We had tried to suggest which we expected would best be done at the factor; however to remove any confusion the asterisks have been removed in the proposed modification to G99.

## Slide 9: Issues for H2 2020 - 2
No | Issue | Assumed Status
93 | Exceptions for output on falling frequency in ECC 6.3.3.1 for CCGTs are not carried forward into the relevant parts of G99 | This is a drafting omission. The Grid Code deals with this appropriately. It is a minor text modification to replicate the Grid Code approach. We will include this in the next modification, subject to any other considerations related to this issue (see issue 96 (a)).
94 | It was recognized in 2018 that both the Grid Code and G99 contained errors in the use of the various terms used for minimum generation. The Grid Code is currently being corrected through a formal modification GC0136. | G99 changes are being been drafted to align with the Grid Code. These will be inserted into G99 at the next opportunity for a modification.

## Slide 10: Issues to be closed
No | Issue | Assumed Status
76 | Section C.6.2.4 states that the internal clock shall be synchronised with UTC via GPS satellite or other functionally similar method. Could it be confirmed that the time accuracy achieved with an NTP server synchronised with UTC via a GPS reference would meet the requirement? | No. We are assuming that the question relates to a local area network (LAN) application with an NTP server synchronised via a GPS reference. Our understanding is that accuracy against UTC may be +/- a few milliseconds for RD connected to the LAN and so would not be suitable. A GPS receiver or radio clock connected direct to the RD is a way to meet the requirement. It also would be possible to meet the requirements solution if a delayed time signal can be accommodated by re-adjusting the accuracy to account for a communication delay. This is to be included in the proposed revision of C.6, to be consulted on over Summer 2020.
87 | The completeness of a PGM in including or excluding a communication device that can also be used to set the GB parameters. | This query has been referred to the manufacturer for clarification/resolution. No further information received. DNOs are aware of the issue and will deal with cases as they arise
88 | We have the experience of DNOs having very different requirements for the compliance information to be submitted – particularly in relation to simulations and frequency compliance information | These issues were discussed in detail at the 26/02/2020 DER Technical Forum. It was noted that many/most of the issues identified to date are being, or have been, addressed. However DNO representatives confirmed their wish to be the key point of contact for owners, developers and manufacturers where it seems that DNOs are not following agreed interpretations of G99
98 | Seek a route for the resolution of G99 technical queries | Formally resolving queries with G99 and other D Code documents is a key responsibility of the DCRP. However the DCRP has accepted that the DER Technical Forum is currently providing this facility through the operation of the forum, and its driving of G99 updates.

## Slide 11: ENA Database and Type Tested Compliance
Placeholder for now
As of 31/10/19 there are over 1000 entries registered from about 50 manufactures into the ENA’s type test database.
ENA wrote to 11 manufacturers about their incomplete etc entries, and asked for resolution of these issues by 5 July 2019. This has resulted in improved resubmissions which are being reviewed.
ENA has appointed engineering consultants to undertake a deeper review of the equipment in the database which started in November 2019. The scope of the review is to
  undertake a review of the Compliance Verification reports registered for each device for completeness and accuracy;
  assess the type test evidence to confirm whether it demonstrates compliance;
  verify the validity of and whether an equipment certificate has been used to demonstrate compliance;
  undertake 2 industry workshops to disseminate learnings of how stakeholders can demonstrate compliance; prepare industry guidance on acceptable type testing methodologies.
The compliance report is to be confidential to the manufacturer and ENA members.
ENA has published guidance on its website re these compliance checks which will be updated based on the consultant’s findings.

## Slide 12: Equipment Certificates
No specific update on this
The ENA has received some queries from organizations engaged in creating equipment certificates for G98 and G99 compliant generating units.
The ENA is supporting those organizations in the expectation that one or more of them will succeed in awarding equipment certificates to one or more manufacturers.

## Slide 13: Other Updates
EU network codes are being reviewed in relation to
  Storage – ie to remove the exclusion on storage
  Removing the 110kV threshold for Type D – at least for plant smaller than 5MW, or more likely 10MW
Future EU codes work includes
  defining what a material alteration is – we have asked that this process recognize the development work this forum did in what is now Appendix A6 to G99.
  Contemplation of extending more type B requirements (particularly fault ride through) to type A
Hard to say if these developments will affect the UK.

## Slide 14: AOB and Next meeting
AOB
  None
Next meeting
  TBA