## Slide 1: DER Technical Forum
30 November
10:00 start
Microsoft Teams meeting
Join on your computer or mobile app
Click here to join the meeting
Or call in (audio only)
+44 20 3855 5885,,989448599# United Kingdom, London
Phone Conference ID: 989 448 599#

## Slide 2: Welcome, Housekeeping and Introductions

## Slide 3: Agenda
1 | 10:00 | Welcome, Introductions and Acceptance of Agenda.
2 | 10:05 | Feedback from special interest session on modelling/simulations (issue 110)
3 | 10:15 | Technical issues surrounding BESS connexions (Issue 114)
4 | 10:45 | New Issues since the last forum: 117, 118, 119, 120, 121 (from AMPS)
5 | 11:05 | Unresolved issues 112, & 115
6 | 11:15 | G100 review – update
7 | 11:20 | Fast track review - update
8 | 11:30 | Distributed Restart
9 | 11:35 | EU Developments
10 | 11:40 | D Code compliance developments - update
11 | 11:45 | AOB
12 | 11:50 | Next Meeting Arrangements

## Slide 4: Special Interest Session on Modelling and Simulations

## Slide 5: Modelling and Simulations
Session held on 02 November.
Key outcomes were:
draft a note outlining the mutual expectations for the creation, use and transfer of models between stakeholders and DNOs (see next 3 slides).
review the practicalities around DNOs requiring models in specific software.
Further action/engagement would be planned via this forum.

## Slide 6: Statement of needs and uses (1)
  In these slides the generation owner is referred to as Generator, and this also includes any agent or developer acting on behalf of the Generator.
The need
  Both DNOs and Generators need to be able to model the behaviour of new generation assets. The Generator has the need to demonstrate compliance with G99 (and/or the Grid Code) via the submission of simulations, and the DNO has an ongoing need to manage the distribution network, taking into account the behaviour of the generation.
  Both of these needs can only be satisfied if a suitable model of the generation equipment is available.
  DNOs’ needs will not be identical in each case: larger generation, and where there is more likely interaction with other connected customers’ devices, particularly other generation, more sophisticated and detailed modelling including transient stability are required. On the other hand, DNOs’ needs to include the effects of smaller generation, with less interaction with other customers’ equipment, might be limited to just load flow and fault level analysis.

## Slide 7: Statement of needs and uses (2)
The legal framework
  DNOs have always required that Generators provide sufficient information to enable DNOs to model appropriately the generation that is being connected. The long standing requirement is in G59 (and G75 before it) and was only generally applied to generation connected at high voltage.
  For synchronous machines the representation of the generation was expected in traditional IEEE transfer function block diagram form.
  The introduction of the EU Network Code, Requirements for all Generators, extends this historic approach and makes the provision of validated models mandatory for both synchronous and non-synchronous generation for all power generating modules of 10MW or greater.
  DNOs use a variety of modelling software packages (see following slides) and require models to be provided in these formats. Although this can be a challenge for the Generator to provide, so far DNOs have no evidence that Generators are unable to do so.

## Slide 8: Statement of needs and uses (3)
Generator/DNO interaction
  Generators will need to populate their models with sufficient network data to enable the appropriate simulations. For the majority of type B generation, the assumed minimum fault level of 50MVA is probably sufficient for the simulations required.
  For type C and D, this might still be sufficient, although more realistic source impedances with respect to the network location might be required for some analyses, particularly power quality: the DNO will provide these on request.
  Early on in the life of a project the final specification of the generation equipment might not be available and both Generator and DNO models will need to be on the basis of the best available information and assumptions. The modelling assumptions and data can be updated as the Generator refines the details of the project.
  As part of the overall compliance process, and before the FON can be issued, the Generator will need to hand over the validated model(s) to the DNO. The DNO is not obliged to do anything with the model at that time – its function is to allow the DNO to undertake future system analysis. However DNOs are likely to do some cursory checks that the model provided converges appropriately, that the documentation supporting it is sufficient, and that it aligns and is consistent with the simulation studies supplied.

## Slide 9: WPD
WPD South West and South Wales
WPD East and West Midlands
Package | Voltage level used at |  |  |  | Compatible with? | Comments
 | 132kV | 33kV | 11kV | LV |  | 
PSSE v34.6.0 (SW) v34.7.0(SWa) | Y | Y |  |  |  | 
DINIS v6,4 |  |  | Y |  |  | Moving to PSS Sincal over the next 3 months
PSS Sincal v17.5 |  |  | Y |  |  | 
Connect LV v1.1.4 |  |  |  | Y |  | Connect LV is a new software package that replaces WinDebut.
Package | Voltage level used at |  |  |  | Compatible with? | Comments
 | 132kV | 33kV | 11kV | LV |  | 
PSSE v34.7.0 | Y | Y |  |  |  | 
IPSA v1.6.7 | Y | Y |  |  |  | In the process of moving to PSSE
DINIS v.6.4 |  |  | Y |  |  | Moving to PSS Sincal over the next 3 months
PSS Sincal v17.5 |  |  | Y |  |  | 
Connect LV v1.1.4 |  |  |  | Y |  | Connect LV is a new software package that replaces WinDebut.

## Slide 10: Electricity North West
Package | Voltage level used at |  |  |  | Compatible with? | Comments
 | 132kV | 33kV | 11kV | LV |  | 
IPSA (transitioning to v2.9) | Y | Y | Y |  | Imports alternative file formats | Routinely used down to primary substation 11kV or 6.6kV bars Used at 11kV, 6.6kV and LV for bespoke analysis and innovation projects. Some use of scripts for automation
Dinis V6.4.4 |  |  | Y |  | Some software can import Dinis files but we don’t have the ability to import other formats into Dinis | Primary substations are modelled with an equivalent source of upstream system fault infeed.
GROND V11_ENW_MARCH_2021 |  |  | Y |  | ? | Although Dinis is the main planning tool for secondary networks, we use Grond for some 6.6/11kV network performance studies and protection studies
In these tables 11kV indicates any voltage above 1kV up to and including 20kV. 33kV includes 66kV

## Slide 11: SPEN
SP Manweb
SP Distribution
Package | Voltage level used at |  |  |  | Compatible with? | Comments
 | 132kV | 33kV | 11kV | LV |  | 
IPSA (mostly v2.9) | Y | Y | Y |  |  | Some analysis is automated using python.
WinDebut |  |  |  | Y |  | Used for some HV connections.
Package | Voltage level used at |  |  |  | Compatible with? | Comments
 | 132kV | 33kV | 11kV | LV |  | 
DIgSILENT Power Factory | Y | Y | Y |  |  | 
WinDebut or Bespoke Excel Workbook in some cases) |  |  |  | Y |  | Used for some HV connections.
In these tables 11kV indicates any voltage above 1kV up to and including 20kV. 33kV includes 66kV

## Slide 12: UKPN
LPN
SPN
Package | Voltage level used at |  |  |  | Compatible with? | Comments
 | 132kV | 33kV | 11kV | LV |  | 
DIgSILENT Power Factory 2019 (SP4) | Y | Y | Y* |  | Previous versions of PowerFactory CIM data exchange capabilities (import/export) PSS/E, Neplan, Sincal (only import) | Various scripts in DPL (DIgSILENT Programming Language) used for automation.
DPLAN2 |  |  | Y | Y |  | *DIgSILENT used for some 11kV generation studies
Dinis (replaced with DPLAN2) |  |  | Y |  |  | Still used for some interconnected network studies.
Voltage Rise Assessment Tool -Bespoke Excel |  |  |  | Y |  | Used by some departments for smaller connections (up to 200kVA) as well as background for the Smart Connect application.
Package | Voltage level used at |  |  |  | Compatible with? | Comments
 | 132kV | 33kV | 11kV | LV |  | 
DIgSILENT Power Factory 2019 (SP4) | Y | Y | Y |  | Previous versions of PowerFactory CIM data exchange capabilities (import/export) PSS/E, Neplan, Sincal (only import) | Various scripts in DPL (DIgSILENT Programming Language) used for automation.
GROND v10 (to be replaced by DPLAN2 |  |  | Y |  | Not sure | Used for demand connections only. DPLAN2 will be used at both 11kV and LV once the migration from GROND is complete.
WinDebut |  |  |  | Y |  | Used for demand connections only.
Voltage Rise Assessment Tool -Bespoke Excel |  |  |  | Y |  | Used by some departments for smaller connections (up to 200kVA) as well as background for the Smart Connect application.

## Slide 13: UKPN - 2
EPN
Package | Voltage level used at |  |  |  | Compatible with? | Comments
 | 132kV | 33kV | 11kV | LV |  | 
DIgSILENT Power Factory 2019 (SP4) | Y | Y | Y |  | Previous versions of PowerFactory CIM data exchange capabilities (import/export) PSS/E, Neplan, Sincal (only import) | Various scripts in DPL (DIgSILENT Programming Language) used for automation.
GROND v10 (to be replaced by DPLAN2 |  |  | Y |  | Not sure | Used for demand connections only. DPLAN2 will be used at both 11kV and LV once the migration from GROND is complete.
WinDebut |  |  |  | Y |  | Used for demand connections only.
Voltage Rise Assessment Tool -Bespoke Excel |  |  |  | Y |  | Used by some departments for smaller connections (up to 200kVA) as well as background for the Smart Connect application.

## Slide 14: Northern Powergrid
Yorkshire
North East
Package | Voltage level used at |  |  |  | Compatible with? | Comments
 | 132kV | 33kV | 11kV | LV |  | 
DINIS v6.4.4 | Y | Y | Y |  |  | 
GROND v8.03 |  |  | Y |  |  | 
Autodesign v1.0 |  |  |  | Y |  | Northern Powergrid own s’ware development. Spreadsheets used for LV too.
Package | Voltage level used at |  |  |  | Compatible with? | Comments
 | 132kV | 33kV | 11kV | LV |  | 
IPSA v2.5.1 | Y | Y |  |  |  | 
DINIS v6.4.4 |  |  | Y |  |  | 
GROND v6.56 |  |  | Y |  |  | 
Autodesign v1.0 |  |  |  | Y |  | Northern Powergrid own s’ware development. Spreadsheets used for LV too.
LV Design v2.2d Beta 5 |  |  |  | Y |  | 
In these tables 11kV indicates any voltage above 1kV up to and including 20kV. 33kV includes 66kV

## Slide 15: SSEN
Package | Voltage level used at |  |  |  | Compatible with? | Comments
 | 132kV | 33kV | 11kV | LV |  | 
PSSE, v33 and v34 | Y | Y | N (software has limitations) |  | CIM data exchange capabilities (import/export) DigSilentPowerfactory(export/import) SINCAL(export/import) | Various Python scripts used automations
DIgSILENT Power Factory | Y | Y | Y | Y Future | CIM data exchange capabilities (import/export) PSSE(import/export) SINCAL import | Various scripts(Python, DPL etc) used for automation.
SINCAL v16, v17 |  |  | Y | Y | PSSE(import/export some limitations) CIM,CYMDIST,DINIS and UCTE import/export DIgSilent Powerfactory | Use mainly for HV networks analysis, including unbalanced network
WinDebut |  |  |  | Y |  | 

## Slide 16: Modelling and Simulations (repcap)
Session held on 02 November.
Key outcomes were:
draft a note outlining the mutual expectations for the creation, use and transfer of models between stakeholders and DNOs.
review the practicalities around DNOs requiring models in specific software.
Further action/engagement would be planned via this forum.

## Slide 17: Battery Energy Storage Systems

## Slide 18: BESS discussion session
A stakeholder/DNO discussion was held on 18 November.
The key focus of the discussion was on the assumptions made about reactive power outputs, and how reactive power outputs changed as active power flows moved from import to export (particularly) and vice versa.
DNOs agreed to consider a number of aspects of the modelling and to report back in a couple of months time.
Action | Owner | Date
Review assumptions re real and reactive swings | DNOs | End of Jan 22
Review suitability of SAF for BESS | ALL | 10 December 2021
Propose SAF updates if appropriate | DNOs | End of Jan 22
Consider BESS in voltage control mode | DNOs | End of Jan 22
Consider if a concept of headroom would help when considering multiple BESS interactions | DNOs | End of Jan 22

## Slide 19: New Issue

## Slide 20: DER Tech Forum – new issues
No | Issue | Draft response
117 | Need of Effective date: Even though the current amendment is classified as minor changes there are significant changes that would require time for manufacturers to update their PGMs to comply with recent requirements. Ex one of those is the Cyber security requirement. For changes like these that would require identifying and implement a solution to an already compliant machine would take significant time/cost. Hence any requirements that would require modification of existing hardware/software design would require an effective date from the current release (a minimum of 6 months is recommended) to enable the manufacturer to be compliant with up-to-date requirements. Currently, the exception is applicable only for certain technologies but is required to be made for all technologies. Please be mindful that it would take manufacturers some time to find an effective solution and to prove compliance. | We agree that any change of requirements will generally need a period before compliance is required to allow manufacturers and others to accommodate the new requirements. As you are probably aware the recent modification to introduce new requirements for storage built in a 12 month period for manufactures and developers to implement any required changes before compliance is required. It might be that this is what you have in mind when you refer to the exception in your last sentence? We do not believe that there are any changes that we have classified as minor in the most recent amendment that impose any new compliance requirements on manufacturers or developers. Even without a specific formal implementation period, manufacturers do have significant warning of even the minor changes. They are all discussed at the DER Technical Forum, often over more than one meeting, and are summarised in the slides for the Forum which are published. The changes are formally consulted on, providing both an opportunity to absorb the proposed changes, to assimilate the implications, and provide a response or challenge to the proposals. There is then a further period, usually a couple of months, before the modification is approved by the regulator and published. In regard of the new references for cybersecurity, there is no new specific performance or compliance requirements added at this time, simply an expectation that manufacturers will be applying industry good practices, as well as standards that manufacturers should already be working to, or adapting to. It might be that the requirements of the network licensees, as provider of critical national infrastructure, do become more specific in the future, but we recognize this is a developing area and we are initially seeking to apply guidance and a light touch. In conjunction with BEIS ENA has produced guidance for Distributed energy resources (DER) cyber security connection at https://www.energynetworks.org/operating-the-networks/managing-cyber-security. However we do note your concern over the most recent change and we will be happy to discuss any points relating to them, or modifications to ENA documents more generally.

## Slide 21: New issues (2)
No | Issue | Draft response
118 | Clarification required on certificate/compliance validity: As it is difficult in managing different requirements at Plant level/PGMs/DNO/manufacturers it is requested to define the duration for the validity of a compliance report/certificate already obtained. | Our current working assumption is that any certification is valid for the working life of the equipment it is associated with, provided that (i) the manufacturer does not change the design or manufacturing techniques such that the original compliance assessment becomes invalid or (ii) the requirements in the Distribution Code (or G99 etc) do not change. In this case we would expect to draw explicit attention to this, as we have for the changes to the requirements for storage. Please note that 2.14 in G99 tries to make it clear that an update to G99 does not require any equipment to be recertified, unless the requirements have fundamentally changed.

## Slide 22: New issues (3)
No | Issue | Draft response
119 | Clarity on how the regulation is applied between releases: Manufacturers normally produce products in mass and it is difficult to keep the products up to date with frequently changing requirements and it is difficult to produce products to suit different regulatory releases either. Moreover, the Stock that would is currently held would be dead. Suppose a plant connection agreement is signed up for Amendment 4 and during the Connection phase and Amendment 8 is released, it would be difficult for manufacturers to produce products to be compliant with both 8 and 4. Similar confusion might arise for DNO while trying to maintain records of what Amendment applies to which plant/product during the FON stage. It is proposed that a similar method for expiry date is adopted from Germany. For example, if a product is certified in 2021 for Amendment 8, then it would be valid for 5 years. During the expiry of the certificate, the product has to be updated to the most recently released version. By doing so, it would be easy to manage the certificates from the Manufacturer side and DNO. | As stated in 117 and 118 above G99 does not require that changes to the drafting of G99 necessarily trigger a need for manufacturers to change anything (unless there has been a misapprehension of the existing requirements). Where there is a need to change equipment, and where there is stock in the supply chain, we would expect to provide sufficient time for manufacturers to be aware and to work the stock through the chain. This is why we provided a 12 month implementation period for the recent changes of requirements for storage. The Requirements for Generators formally provided a mechanism for plant in construction under a contract struck before the implementation date of the RfG could retain the pre-RfG requirements. This seems equitable and sensible and therefore it might be worth drafting an approach based on this principle into G99. Thank you for the suggestion re certification in terms of the German approach. We believe it introduces an automatically driven new workload for manufacturers, and in many cases would add little given the approach outlined in the above answers.

## Slide 23: New issues (4)
No | Issue | Draft response
120 | Regulated releases dates and updates to G99 It is recommended that G99 changes happen Annually or every 3 or 5 years similar to other regions in Europe. In the future, we would like to understand if there would be sudden releases similar to Amendment 7 and Amendment 8? If so, can it be avoided and change made annually or few years in once as there might be a difficulty for the users to keep up with the changes? Similar to Italy, is it possible just to release the version with details of what the new changes are instead of a complete release of an existing standard. This would be easier for DNO/Supplier/User to understand what is new between the baseline version and new amendments. The current version has changes in the revision table which is not covered in the document hence it is confusing. | 2021 was an exceptional year where we issued a number of versions which dealt with both legal and minor technical issues or provided clarification of clauses. We are very aware of the frequency of G99 amendments, and we also would like to restrict them to about one per year. G99 is subtly different to a conventional technical standard. It actually implements legal obligations that generation owners (and DNOs) have to meet. If a problem with its interpretation or implementation is brought to our attention, generally we need to deal with it expediently; otherwise the legal interpretation of the requirements might be misaligned with the actual requirements – and this can have an effect on developers who have projects in development that might being adversely affected by the text that needs modifying. G99 implemented a significant change in the requirements for generation in GB and took effect just over two years ago. Initially there were many queries raised, but the amendments made to date have generally now addressed most of these and we expect the pace of necessary changes to reduce. As regards understand the changes, the consultation version of the documents include full tracked changes, and the consultation paper explains each change and its relevance. However it might be helpful for us to publish as final change tracked version of the latest issue alongside the approved new version. This would provide a simple check for users as to what has changed from the text they are familiar with. We are currently exploring the option of publishing a track-changed version of the new documents alongside the Report to Authority documents on the Distribution Code website (http://www.dcode.org.uk/).

## Slide 24: New issues (5)
No | Issue | Draft response
121 | Minor corrections in G99 It is proposed to replace all "electricity storage devices" with "Energy storage devices". Currently, all the devices store the electricity in alternative energy form not as electric/charge form directly. Clarification on which requirements apply for Energy storage devices. As the word is included in synchronous machine and power pack modules. Synchronous machine working is limited by the machine's ability to fulfill grid codes, but convertor-based devices can be altered to fulfill stringent requirements due to electronic capability. Hence for devices that employing different technologies, it is recommended to keep the requirements separately and not to mix them. Clarity on what is the acceptable minimum level of cyber security required at the power generating module. Is it required for the power gen and the power generating control system components to be at the same security level as the facility and the ENA network? | G99 is a network oriented documented and as such it is blind to the storage medium. From the network perspective storage consumes electricity when charging, and produces electricity when discharging – ie a flow of electricity in and out. Energy storage includes heat storage, and electric vehicles, where the final output is heat and mechanical energy respectively, not electricity. The wording of the synchronous power generating module has been chosen deliberately to cater for technologies such as compressed air storage where the same synchronous machine is used for compression and expansion. In all cases the power generating module has to meet all the requirements for that technology, irrespective of how it is constituted. There are no specific requirements in G99 or G98 in relation to cybersecurity; only a general obligation to manage cyber risks appropriately.

## Slide 25: New issues (6)
No | Issue | Draft response
121 | Gas turbine can work independent of Heat recovery system and might start working before HR blocks starts. Hence recommended to show as two different modules instead of one. As once synchronized, it is possible for GT to run independently from the HR block. Modification of synchronous power generating module definition: recommend to remove energy storage device unless it is a flywheel like device that would be used as power generating device (ex. Mechanical UPS system - rotary UPS) but these devices are least used against grid as it supports power backup for short duration and just a load on grid until the grid fails. | Figure 4.1a shows a single power generating module comprising two separate power generating units. Whilst it is true that the gas turbine unit can be run independently, it is assumed that the steam turbine cannot. If the steam turbine were capable of independent operation then there would indeed be two separate synchronous PGMs. However as the steam turbine (a) cannot run independently and (b) normally runs in tandem with the gas turbine, the two units comprise a single SPGM. As per (a) above the definition caters for technologies such as hydro pumped storage and compressed air storage. Short term energy storage devices such as flywheels, DRUPs etc are specifically excluded from G99 – see section 7.1.2: “Equipment other than Generating Units (eg traction loads, lift motors etc) may act as a short term source of energy, and inject electrical energy into the Customer’s Installation when they operate in a regenerative mode. In general EREC G99 will not apply as there will be no need to make any specific design accommodation for such equipment as it is unlikely that they will support any possible power island for a significant length of time. Where such equipment can act as a source of electrical energy for more than a few seconds (say typically 20 s), the DNO will advise the Customer if the Customer’s Installation requires any special consideration such as reverse power protection on a case by case basis.”

## Slide 26: Previous Issues

## Slide 27: Outstanding Issues - 1.
No | Issue | Assumed Status
110 | There is uncertainty over the detail which needs to be submitted for type C and D compliance simulations – particularly the supporting information about the models which could be considered to be the consultants’ IPR. | Although simulations and their models have been discussed several times, and there are a few entries in this log, it might be worth holding a review of what is considered to be appropriate good practice in this area with appropriate stakeholder and DNO experts. Stakeholders will be canvassed to gauge interest in a dedicated session to develop this.

## Slide 28: Outstanding Issues - 2.
No | Issue | Assumed Status
113 | P28 has the usual classifications of frequent events, infrequent events (4 per month) and very infrequent events (1 per 3 month)…. what should we be assessing a storage system performing a dynamic containment service as? The UK grid is reasonably stable, at the moment, but with more conventional plant dropping out, the power swings are going to get a bit more sever, and the DC type services will be getting worked more often. Classing it as a very infrequent event probably isn’t realistic, but what about infrequent events? I could see that it is possible that you could get to around the 4 events per month, although probably not at the full power swing. | This is a good point, and one that probably would benefit from a consistent consideration by DNOs. It might be sensible to base the frequency on the observed incidence of frequency excursions, over the last 18 months say, that trigger a specific level of response from such services. The response level might be set locally, and the P28 “frequency of event” set by the historic track of frequency excursions triggering that level of response. This can be calculated from the information NGESO publish monthly. This should be picked up as part of ongoing work to develop a common approach to BESSs between the DNOs. However, note that in the BESS discussions on 18/11 it was pointed out that the 3% limit essentially applies at any time once the transients have died away, so for BESS power swings the 3% probably applies in all cases, irrespective of frequency of event.

## Slide 29: Outstanding Issues - 3.
No | Issue | Assumed Status
114 | We have concerns relating the voltage step change for Battery Energy Storage Systems (BESS) when the systems are designated for fast frequency response. A number of network operators define step change to be full declared export to full declared import for real power P and for reactive power Q. The FFR contracts do not have a contracted obligation to reverse the direction of reactive power flow and no obligation to match the fast MW response with a MVAr response. When importing, there is no obligation to operate at a particular power factor only to operate within a +/-0.95 range. If a full MW ramp has occurred, it is reasonable to assume the system is under stress. To reverse Q at this point would be the worst of all strategies at it would exacerbate the stress of the system by introducing an unnecessary voltage step. It is likely that EFR or FFR BESS is located at a point with a high X/R ratio (close to a BSP or GSP). Therefore a unit change in Q would have at least 10x the impact on at the voltage step that of a unit change in P. This Q reversal condition appears to be based on a false assumption about the default behaviour of inverters under FFR. We believe it is a matter for the customer to demonstrate through simulation the voltage step change under power reversal. It is a matter for the customer to produce a reactive power strategy that meets the constraints of the D Code and the connection offer. Confirmation of the simulation can be done via commissioning tests with frequency injection for smaller steps. The imposition of this requirement distorts the market by essentially limiting the capacity of a BESS scheme to around half the capacity of other technologies thus creating hidden barrier to the penetration of the technology. The customer should demonstrate how they meet the voltage step change challenge through modelling and if necessary to verify through commissioning demonstration, not for the network operator to impose a control philosophy. | To be picked up in the BESS sessions

## Slide 30: Outstanding Issues - 4.
No | Issue | Assumed Status
112 | A common issue that keeps coming up is Registered Capacity vs design install and grid agreements. I have a specific case where the G99 and connection agreement is for 9MW, the developer undersized the inverters slightly. So it can only produce 8.5MW ( in round numbers) whilst operating in the 0.95 lag/lead range. This is what is shown when we do the G99 study, and we noted this shortfall. So the question arises, of what happens to the site now and what can it do. Specifically, 1) Is it’s new official RC 9MW or 8.5MW I.e do they retain their original agreed capacity, or is this list back to the DNO? This is a common sticking point, taking the above example it cannot meet the 9MW required, but they may upgrade an inverter later to give them more MVAr headroom and it could then operate at 9MW. 2) If the DNO doesn’t want/need them to operate across the 0.95 lag/lead range can they then operate at 9MW active power and say unity or 0.98pf. In this case they are producing their official R, but their system design does not meet the required G99 standard for a 9MW site. | This is an issue that does re-appear from time to time. We have attempted to deal with it in the past in issues 40, 80 and 83. We went through it with slides at the 7 June DER TF. DNOs have summarized how they specify maximum capacities and power factors in their connexion agreements We propose that we incorporate the material from the 7 June meeting into the next version of the DG See next 9 slides (07/06 material slightly updated and expanded):

## Slide 31: Registered Capacity
Was revised in G99/1-6 March 2020
Registered Capacity (Pmax)
The normal maximum Active Power capacity of a either a Power Generating Module (in the case of a Power Park Module, the lesser of the Inverter(s) rating or the rating of the energy source), or of a Power Generating Facility, as declared by the Generator taking into account the Active Power consumed when producing the same and the production of the required Reactive Power at the Connection Point.

## Slide 32: Losses due to Impedance between Inverters and Connection Point need to be accounted for (1/3)
Nominal “40 MW” of PV connected at 132 kV – ie actually 40 MW at unity PF; 40 MVA
Power Generating Module (PGM) / Power Park Module (PPM)
Power Generating Facility (PGF)
132 kV CP
Connection Point
Required pf = 0.95
Active Power at CP is 37.80 MW
Reactive Power at 0.95 pf is 12.43MVAr
40.00 MVA
Assume 5% loss in MVAr in cables and across transformer
Active power is 37.80 MW
Reactive power is 13.08 MVAr
Registered Capacity is 37.80 MW

## Slide 33: Losses due to Impedance between Inverters and Connection Point need to be accounted for (2/3)
If at least 40 MW is to be exported:
Power Generating Module (PGM) / Power Park Module (PPM)
Power Generating Facility (PGF)
40.00 MW
Connection Point
0.95 pf
Required reactive power 13.15 MVAr
42.11 MVA
Assume 5% loss in MVAr in cables and across transformer
40.00 MW
13.84 MVAr
42.33 MVA
Registered Capacity is 40.00 MW
Need to have 42.33 MVA of inverter capacity.
132 kV CP

## Slide 34: Losses due to Impedance between Inverters and Connection Point need to be accounted for (3/3)
If at least 40MW is to be exported and TX losses are not negligible:
Power Generating Module (PGM) / Power Park Module (PPM)
Power Generating Facility (PGF)
132 kV CP
Connection Point
Required pf = 0.95
Active Power at CP is 40.00 MW
Reactive Power at 0.95 pf is 13.15 MVAr
43.10 MVA
Assume 2% loss in MW and 5% loss in MVAr in cables and across transformer
Active power is 40.82 MW
Reactive power is 13.85 MVAr
Registered Capacity is 40.00 MW
Need to have 43.10 MVA of inverter capacity.

## Slide 35: How to approach inverter sizing – example 40 MW desired output
40MW of metered export is desired, but this needs to account for the power factor range required, and the reactive loss in the transformer.
If the site expects to run normally at fixed pf, use this pf to determine the MVA required; eg if 40 MW of metered export is required at 0.98 pf leading, then this requires 40.81 MVA of capability. However in order to be compliant with G99 the site also has to be capable of operating at 0.95 pf – which would result in 38.77 MW exported.
The inverter(s) needs to be sized for 42.33 MVA, which of course is 42.33 MW at unity pf.
Assuming no resistive losses between the inverter(s) and the connexion point, the Registered Capacity of the Power Generating Module is 38.77 MW.
However the maximum export capacity can be agreed to be 40.81 MVA at 0.98 pf. This will allow export of 40 MW at the required power factor.
If there are auxiliary supplies and other reactive (or real) losses on the Generator’s system these will need to be factored in and the inverter(s) upsized if the metered output is to be maintained.

## Slide 36: Ratings for 40MW export at 0.98pf
40MW at 0.98pf at the connection point
Power Generating Module (PGM) / Power Park Module (PPM)
Power Generating Facility (PGF)
40.00 MW
Connection Point
0.98 pf
Required reactive power 8.11 MVAr
40.81 MVA
Assume 5% loss in MVAr in cables and across transformer
40.00 MW
8.53 MVAr
40.90 MVA
0.978 pf
Registered Capacity is 38.77 MW
Need to have 42.33 MVA of inverter capacity for compliance with the ±0.95 pf requirement.
132 kV CP

## Slide 37: Representation on circle diagram (for the connection point)
40 MW
38.77 MW Registered Capacity
40.81 MVA capability locus
At PGM terminals: 40.90MVA, 0.978 pf
Active power
Lagging reactive power
Leading reactive power
Reactive range ± 0.95 pf
Desired operating point: 40 MW, 0.98 pf

## Slide 38: Connection Contract for the 40 MW example
Maximum Export Capacity (MEC) is something to be agreed between the DNO and the Generator. For this site it could be either
  40.81 MVA @ 0.98 pf (ie 40 MW)
Or
  40.81 MVA @ 0.95 pf (ie 38.77 MW)
The first of these is probably more useful, particularly if this is the agreed expected normal operating regime, recognizing that capability to operate at 0.95 pf is a G99 requirement anyway
The Registered Capacity of the PGM is 38.77 MW
The Registered Capacity of the site (for triggering medium or large classification) is also 38.77 MW (assuming no other generation on site)

## Slide 39: Registered Capacity – proposed note for guides
Registered Capacity is the Active Power (kW) of the Power Generating Module (or Facility). A technical capability of 0.95 power factor is generally required at the Connection Point.
There could be an active and reactive power loss between the Power Generating Module and the Connection Point. The active power loss is small and usually ignored in practice.
The Standard Application Form asks for maximum active and reactive export power as well as the Registered Capacity and notes that the Registered Capacity can apply to:
a Power Generating Facility. This is the total maximum Active Power capacity of the Power Generating Module(s) in the Power Generating Facility, minus the (parasitic) power consumed by the generation process. For a Power Generating Facility with no other site demand you should take account of the requirement to produce Reactive Power at the Connection Point which will mean considering other equipment such as transformers and cables connecting the Generating Units to the Connection Point. For a Power Generating Facility embedded in a private network with demand it is recommended that you discuss the requirement for the production of Reactive Power with the DNO. Hence the Registered Capacity (kW) will generally be less the than Apparent Power (kVA).
a Power Generating Module. This is the maximum Active Power capacity of the Generating Unit(s) comprising the Power Generating Module, minus the (parasitic) power consumed by the generation process. It needs to take account of the requirement to produce Reactive Power, and whether this is at the Connection Point or at the Module terminals. Hence the Registered Capacity (kW) will generally be less than the Apparent Power (kVA). Where a Power Generating Module comprises inverters, the maximum Active Power capacity of the Generating Unit(s) is the lesser of the Inverter(s) rating or the rating of the energy source.

## Slide 40: Update on G100 review and Fast Track

## Slide 41: G100
Last formal meeting 08 September.
The first consultation produced very effective input from 7 stakeholders and 2 DNOs.
Most responses contain a mix of strategic issues and specific points of detail.
The strategic issues relate principally to the development of demand side services in Great Britain, and the possibility of G100 having adverse interactions here.
In particular:
  Excessive mode 2 excursions counterproductive as drafted.
  Need to not hinder the development of EV smart charging (EV Energy Task Force)
  Queries re PAS 1878 and 1879 development and adoption by the wider industry
  Approaches to cyber security and EN303 645,
Key outcome of the 23/07 WG meeting reviewing the above was agreement to allow 5s excursion into mode 2 before classing as an excursion counting towards excessive excursions.
Modes renamed as States.
A second consultation was published on 08 October, closing on 03 December.

## Slide 42: Fast Track
Broad DNO agreement on lifting the export limit to 32A total generation, or up to 60A if G100 limitation scheme employed to limit export to 32A.
Existing fast track criteria still exist – so aggregate generation <32A and a G100 scheme set to 16A has automatic acceptance of the application within 10 days.
The new proposed fast track will subject applications to a triage process within 10 days. Most will easily pass, but some, where the system is weak, will need normal formal assessment and quotation.
The triage process will allow for other considerations, such as local saturation and power quality, to be considered.
A DCRP consultation on the proposals closed on 12 November and DNOs are considering the responses, which were supportive but with some detailed suggestions.

## Slide 43: GC0117

## Slide 44: Grid Code Modification Proposal GC0117
Objective is to align the definition of Small and Large across GB.
Two key proposals being considered:
    Lower the Large threshold to 10MW in England and Wales
    Raise the 10MW and 30MW threshold in Scotland to 100MW
NGESO are arguing for the first of these options.
The effect would be that any generation ≥ 10MW would have to
  Accede to the CUSC, and comply with all its requirements
  Be part of the Balancing Mechanism
  Provide data directly to NGESO
Consultation on the proposals is expected early in the New Year.

## Slide 45: Distributed ReStart Project

## Slide 46: Distributed Restart Project -1
Introduces the concept of an Anchor Generator, which is an embedded PGM cable of self starting and re-energising the DNO’s system, supplying DNO’s customers, and ideally being able to re-energize an element of the transmission system.
The Project’s working assumption is that such PGMs might be as small as 2MW.
The draft requirements are being incorporated into Grid Code OC9 (black start) and OC5 (testing).
If all formal participants of a distributed restart zone (DRZ) are CUSC parties, there is arguably no overwhelming need to place requirements in the D Code. However, in both the interests of not limiting the approach to CUSC parties, and transparency and clarity, it seems highly desirable to create harmonized requirements in DOC9 and DOC5.

## Slide 47: Distributed Restart Project - 2
The Project is feeding into GC0148 (E&R Implementation – a joint GCRP/DCRP WG) to introduce the Grid and Distribution Code modifications.
NGESO also have to respond to their new Electricity System Restart licence condition, which might lead to a change of status and ambition for the project.
NGESO has mentioned the touch point too with GC0117 in terms of where an embedded PGM will become Large in future (potentially 10MW).
G99 (and G59) largely avoids direct conflict with DRZ requirements, but would benefit from a few tweaks (particularly to the definition of its scope) to remove any possible confusion.
The project completed draft amendments of the Grid Code, D Code, G59 and G99 which will form part of the formal consultations of GC0148.

## Slide 48: EU Developments

## Slide 49: EU developments
A new draft EU network code on cybersecurity is out for comment until 10 December.
There are three new expert groups starting that are likely to feed revisions into the EU Network Codes:
  Harmonization of certification and family groupings
  Advanced grid services and controls for grids with a high penetration of DER
  Connexion issues for offshore systems.
The third of these is unlikely to have any impact on DNOs and their stakeholders.

## Slide 50: Distribution Code Compliance

## Slide 51: Distribution Code Compliance
Background:
  The accelerated loss of mains programme requires that all generation in GB retrospectively adopts new loss of mains protection arrangements.
  In some cases these changes are not trivial.
  In some cases owners might ignore the requirements.
  DNOs have not had a strong historic need to rigorously enforce D Code compliance, and lack the legal tools and experience to routinely challenge non-compliances, both in general, but specifically for loss of mains protection.
Solution
  Modification DCRP/21/05/PC proposes D Code text that works through a managed compliance process over six months.
  Subject to appropriate checks and balances, if compliance not achieved in this timescale, the customer can be disconnected by the DNO.
  Following public consultation the DNOs will be submitting the modification to Ofgem for approval around the beginning of December

## Slide 52: Wrap up:

## Slide 53: Minutes of previous meeting and actions
Outstanding matters arising not on the agenda:
  None?

## Slide 54: AOB and next meeting
AOB
None?
Next meeting? Early February?

## Slide 55
© ENA 2020