## Slide 1: DER Technical Forum
24 February 2022
14:00 start
Microsoft Teams meeting
Join on your computer or mobile app
Click here to join the meeting
Or call in (audio only)
+44 20 3855 5885,,161001594# United Kingdom, London
Phone Conference ID: 161 001 594#

## Slide 2: Welcome, Housekeeping and Introductions

## Slide 3: Agenda
1 | 14:00 | Welcome, introductions and acceptance of agenda.
2 | 14:05 | Digitalisation of connections
3 | 14:20 | BESS connection issues
4 | 14:30 | System modelling challenges - update
5 | 14:35 | New Issues since the last forum: 122
6 | 14:45 | Unresolved issues 112 - 121
7 | 15:10 | Update on relevant topics: G100 Fastrack storage etc connexions GC0117 Distributed ReStart D Code compliance EU Developments
8 | 15:25 | AOB
9 | 15:30 | Next meeting arrangements

## Slide 4: Digitalization of Connections

## Slide 5: Battery Energy Storage Systems

## Slide 6: BESS discussion session
A session with stakeholders was held on 11 February 2022
The following points were discussed:
  Upstream capacity – it was agreed that pro tem the existing treatment of this in the standard application form remains appropriate as a basis for the discussion on this topic which DNOs and developers need to have.
  Reactive power operating requirements – the DNOs’ proposals for modifying the SAF to capture developers’ initial views as a prompt for appropriate design discussions was accepted by stakeholders, noting that restrictions on VAr flows might be needed to be included in the connexion agreement.
  Simultaneous battery operation and resultant voltage changes – DNOs agreed to give this more thought.
  Voltage control approach – agreed that again pro tem this needs to be approached bilaterally as each DNO, and even networks within a DNO, have different historic design approaches and needs.
Next meeting to be scheduled for 13 April 2022

## Slide 7: Special Interest Session on Modelling and Simulations

## Slide 8: Modelling and Simulations
The outcomes of the special interest session held on 18 November were fed back to the DER last Technical Forum (30/11/21.)
Having reviewed the discussions, DNOs are not sure there is any need for further plenary follow up at this time.
There were two outstanding issues:
  the extent to which CIM might be a solution to some/most of the interoperability problems – but this is a developing area, not least with Ofgem – so progress will follow the external timetable.
  What to do when both NGESO and the DNO need models – in different software. Having reviewed the legal underpinnings, pro tem there does not seem to be any obvious solution other than discussion/negotiation on a case by case basis as both network licensees are entitled to models in their designated software.

## Slide 9: New Issue

## Slide 10: New Issue
Q I represent a UK water industry working group responsible for the development and maintenance of electrical specifications. During recent work to update a specification for low voltage diesel generator sets, I was asked by the group to lobby the ENA technical committee responsible for G99 to consider relaxing clause 7.3.3.1 in EREC G99.
A
7.3.3.1 The Power Generating Module may be permitted to operate in parallel with the Distribution Network for no more than 5 minutes in any month, and no more frequently than once per week. If the duration of parallel connection exceeds this period, or this frequency, then the Power Generating Module shall be considered as if it is, or can be, operated in long-term parallel operation mode. An alternative frequency and duration may be agreed between the DNO and the Generator taking account of particular site circumstances and Power Generating Module design. An electrical time interlock should be installed to ensure that the period of parallel operation does not exceed the agreed period. The timer should be a separate device from the changeover control system such that failure of the auto changeover system will not prevent the parallel being broken.
Notice that the highlighted text already allows for an agreement between the DNO and Generator to agree an appropriate testing regime, subject to there being a valid reason to do so. An alternative would be to fit full LoM protection and address any relevant points from 7.3.3.4, in which case the PGM would be treated as LTP.

## Slide 11: Previous Issues

## Slide 12: Outstanding Issues - 1.
No | Issue | Assumed Status
113 | P28 has the usual classifications of frequent events, infrequent events (4 per month) and very infrequent events (1 per 3 month)…. what should we be assessing a storage system performing a dynamic containment service as? The UK grid is reasonably stable, at the moment, but with more conventional plant dropping out, the power swings are going to get a bit more sever, and the DC type services will be getting worked more often. Classing it as a very infrequent event probably isn’t realistic, but what about infrequent events? I could see that it is possible that you could get to around the 4 events per month, although probably not at the full power swing. | This is a good point, and one that probably would benefit from a consistent consideration by DNOs. It might be sensible to base the frequency on the observed incidence of frequency excursions, over the last 18 months say, that trigger a specific level of response from such services. The response level might be set locally, and the P28 “frequency of event” set by the historic track of frequency excursions triggering that level of response. This can be calculated from the information NGESO publish monthly. This should be picked up as part of ongoing work to develop a common approach to BESSs between the DNOs. However, note that in the BESS discussions on 18/11 it was pointed out that the 3% limit essentially applies at any time once the transients have died away, so for BESS power swings the 3% probably applies in all cases, irrespective of frequency of event.

## Slide 13: Outstanding Issues - 2.
No | Issue | Assumed Status
114 | We have concerns relating the voltage step change for Battery Energy Storage Systems (BESS) when the systems are designated for fast frequency response. A number of network operators define step change to be full declared export to full declared import for real power P and for reactive power Q. The FFR contracts do not have a contracted obligation to reverse the direction of reactive power flow and no obligation to match the fast MW response with a MVAr response. When importing, there is no obligation to operate at a particular power factor only to operate within a +/-0.95 range. If a full MW ramp has occurred, it is reasonable to assume the system is under stress. To reverse Q at this point would be the worst of all strategies at it would exacerbate the stress of the system by introducing an unnecessary voltage step. It is likely that EFR or FFR BESS is located at a point with a high X/R ratio (close to a BSP or GSP). Therefore a unit change in Q would have at least 10x the impact on at the voltage step that of a unit change in P. This Q reversal condition appears to be based on a false assumption about the default behaviour of inverters under FFR. We believe it is a matter for the customer to demonstrate through simulation the voltage step change under power reversal. It is a matter for the customer to produce a reactive power strategy that meets the constraints of the D Code and the connection offer. Confirmation of the simulation can be done via commissioning tests with frequency injection for smaller steps. The imposition of this requirement distorts the market by essentially limiting the capacity of a BESS scheme to around half the capacity of other technologies thus creating hidden barrier to the penetration of the technology. The customer should demonstrate how they meet the voltage step change challenge through modelling and if necessary to verify through commissioning demonstration, not for the network operator to impose a control philosophy. | To be picked up in the BESS sessions

## Slide 14: Outstanding Issues - 3.
No | Issue | Assumed Status
112 | A common issue that keeps coming up is Registered Capacity vs design install and grid agreements. I have a specific case where the G99 and connection agreement is for 9MW, the developer undersized the inverters slightly. So it can only produce 8.5MW ( in round numbers) whilst operating in the 0.95 lag/lead range. This is what is shown when we do the G99 study, and we noted this shortfall. So the question arises, of what happens to the site now and what can it do. Specifically, 1) Is it’s new official RC 9MW or 8.5MW I.e do they retain their original agreed capacity, or is this list back to the DNO? This is a common sticking point, taking the above example it cannot meet the 9MW required, but they may upgrade an inverter later to give them more MVAr headroom and it could then operate at 9MW. 2) If the DNO doesn’t want/need them to operate across the 0.95 lag/lead range can they then operate at 9MW active power and say unity or 0.98pf. In this case they are producing their official R, but their system design does not meet the required G99 standard for a 9MW site. | This is an issue that does re-appear from time to time. We have attempted to deal with it in the past in issues 40, 80 and 83. We went through it with slides at the 7 June DER TF. DNOs have summarized how they specify maximum capacities and power factors in their connexion agreements We propose that we incorporate the material from the 7 June meeting into the next version of the DG See next 19 slides (previous material slightly updated and expanded, including examples with site demand):

## Slide 15: Registered Capacity and Maximum Capacity: Principles
Registered Capacity
  is the size of a PGM or PGF that determines it technical requirements for compliance with the Distribution Code (or Grid Code and/or licensing legislation). It is related to the effect that the PGM or PGF has on the total system – generally in response to short term phenomena. Hence the presence of local on-site load to Registered Capacity is irrelevant*.
Maximum import or export capacities
  these relate principally to the thermal and consequential voltage related effects of power flows on licensees’ networks, so these capacities rightly focus on the net flows at the site/facility boundary, which of course are dependent entirely on the local on-site demand as well as the generation.
  *see later slide

## Slide 16: Registered Capacity and Maximum Capacity: Factors
Permutations:
  Mixture of PGMs in a PGF
  Amalgamated GUs into one or more PGMs
  Site loads (or not)
  Contracted export and import limits for the site
  Physical limitation (eg G100) of export from PGMs
  Physical limitation (eg G100) of export from the site (PGF)
  Storage – ie devices that can be load or generation – amalgamated in to a PGM, or not.
  Values to be defined
  Registered Capacity of PGM (RC)
  Registered Capacity of site or facility (PGF)
  Site maximum import capacity (MIC)
  Site maximum export capacity (MEC)

## Slide 17: Registered Capacity and Reactive Capability

## Slide 18: Current Definition: Registered Capacity
Was revised in G99/1-6 March 2020
Registered Capacity (Pmax)
The normal maximum Active Power capacity of a either a Power Generating Module (in the case of a Power Park Module, the lesser of the Inverter(s) rating or the rating of the energy source), or of a Power Generating Facility, as declared by the Generator taking into account the Active Power consumed when producing the same and the production of the required Reactive Power at the Connection Point.
Note that NGESO are currently reviewing their view of Registered Capacity as applied to a Power Generating Facility – if they decide to change it (to include some element of netting of demand) then DNOs might follow (as it is really for NGESO and licensing purposes that this definition exists).

## Slide 19: Losses due to Impedance between Inverters and Connection Point need to be accounted for (1/3)
Nominal “40 MW” of PV connected at 132 kV – ie actually 40 MW at unity PF; 40 MVA
Power Generating Module (PGM) / Power Park Module (PPM)
Power Generating Facility (PGF)
132 kV CP
Connection Point
Required pf = 0.95
Active Power at CP is 37.80 MW
Reactive Power at 0.95 pf is 12.43MVAr
40.00 MVA
Assume 5% loss in MVAr in cables and across transformer
Active power is 37.80 MW
Reactive power is 13.08 MVAr
Registered Capacity of PPM is 37.80 MW
(and of the site, since there is no active power loss across the TX)

## Slide 20: Losses due to Impedance between Inverters and Connection Point need to be accounted for (2/3)
If at least 40 MW is to be exported:
Power Generating Module (PGM) / Power Park Module (PPM)
Power Generating Facility (PGF)
40.00 MW
Connection Point
0.95 pf
Required reactive power 13.15 MVAr
42.11 MVA
Assume 5% loss in MVAr in cables and across transformer
40.00 MW
13.84 MVAr
42.33 MVA
Registered Capacity of facility is 40.00 MW
Need to have 42.33 MVA of inverter capacity.
132 kV CP

## Slide 21: Losses due to Impedance between Inverters and Connection Point need to be accounted for (3/3)
If at least 40MW is to be exported and TX losses are not negligible:
Power Generating Module (PGM) / Power Park Module (PPM)
Power Generating Facility (PGF)
132 kV CP
Connection Point
Required pf = 0.95
Active Power at CP is 40.00 MW
Reactive Power at 0.95 pf is 13.15 MVAr
43.10 MVA
Assume 2% loss in MW and 5% loss in MVAr in cables and across transformer
Active power is 40.82 MW
Reactive power is 13.85 MVAr
Registered Capacity of PGM is 40.82 MW
Registered Capacity of facility is 40.00 MW
Need to have 43.10 MVA of inverter capacity.

## Slide 22: How to approach inverter sizing – example 40 MW desired output
40MW of metered export is desired, but this needs to account for the power factor range required, and the reactive loss in the transformer.
If the site expects to run normally at fixed pf, use this pf to determine the MVA required; eg if 40 MW of metered export is required at 0.98 pf leading, then this requires 40.81 MVA of capability. However in order to be compliant with G99 the site also has to be capable of operating at 0.95 pf – which would result in 38.77 MW exported.
The inverter(s) needs to be sized for 42.33 MVA, which of course is 42.33 MW at unity pf.
Assuming no resistive losses between the inverter(s) and the connexion point, the Registered Capacity of the Power Generating Module is 38.77 MW.
However the maximum export capacity can be agreed to be 40.81 MVA at 0.98 pf (leading). This will allow export of 40 MW at the required power factor.
If there are auxiliary supplies and other reactive (or real) losses on the Generator’s system these will need to be factored in and the inverter(s) upsized if the metered output is to be maintained.

## Slide 23: Ratings for 40MW desired export at 0.98pf
40MW at 0.98pf at the connection point
Power Generating Module (PGM) / Power Park Module (PPM)
Power Generating Facility (PGF)
40.00 MW
Connection Point
0.98 pf
Required reactive power 8.11 MVAr
40.81 MVA
Assume 5% loss in MVAr in cables and across transformer
40.00 MW
8.53 MVAr
40.90 MVA
0.978 pf
Registered Capacity of PPM (and facility) is 38.77 MW
Need to have 42.33 MVA of inverter capacity for compliance with the ±0.95 pf requirement.
132 kV CP

## Slide 24: Representation on circle diagram (for the connection point)
40 MW
38.77 MW Registered Capacity
40.81 MVA capability locus
At PGM terminals: 40.90MVA, 0.978 pf
Active power
Lagging reactive power
Leading reactive power
Reactive range ± 0.95 pf
Desired operating point: 40 MW, 0.98 pf

## Slide 25: Connection Contract for the 40 MW example
Maximum Export Capacity (MEC) is something to be agreed between the DNO and the Generator. For this site it could be either
  40.81 MVA @ 0.98 pf (ie 40 MW)
Or
  40.81 MVA @ 0.95 pf (ie 38.77 MW)
The first of these is probably more useful, particularly if this is the agreed expected normal operating regime, recognizing that capability to operate at 0.95 pf is a G99 requirement anyway
The Registered Capacity of the PGM is 38.77 MW
The Registered Capacity of the facility (for triggering medium or large power station classification) is also 38.77 MW (assuming no other generation on site)

## Slide 26: Registered Capacity – proposed note for guides
Registered Capacity is the Active Power (kW) of the Power Generating Module (or Facility). A technical capability of 0.95 power factor is generally required at the Connection Point.
There could be an active and reactive power loss between the Power Generating Module and the Connection Point. The active power loss is small and usually ignored in practice.
The Standard Application Form asks for maximum active and reactive export power as well as the Registered Capacity and notes that the Registered Capacity can apply to:
a Power Generating Facility. This is the total maximum Active Power capacity of the Power Generating Module(s) in the Power Generating Facility, minus the (parasitic) power consumed by the generation process. For a Power Generating Facility with no other site demand you should take account of the requirement to produce Reactive Power at the Connection Point which will mean considering other equipment such as transformers and cables connecting the Generating Units to the Connection Point. For a Power Generating Facility embedded in a private network with demand it is recommended that you discuss the requirement for the production of Reactive Power with the DNO. Hence the Registered Capacity (kW) will generally be less the than Apparent Power (kVA).
a Power Generating Module. This is the maximum Active Power capacity of the Generating Unit(s) comprising the Power Generating Module, minus the (parasitic) power consumed by the generation process. It needs to take account of the requirement to produce Reactive Power, and whether this is at the Connection Point or at the Module terminals. Hence the Registered Capacity (kW) will generally be less than the Apparent Power (kVA). Where a Power Generating Module comprises inverters, the maximum Active Power capacity of the Generating Unit(s) is the lesser of the Inverter(s) rating or the rating of the energy source.

## Slide 27: Examples of RCs of PGMs and Facilities, including where there is demand in the Facility.

## Slide 28: PPM and SPGM
Power Generating Module (PGM)
Power Generating Facility (PGF)
PPM capacity is X MVA (ie 2 x X/2 MVA)
SGPM capacity is Y MVA
RC of PPM is X x pfx MW
RC of SPGM is Y x pfy MW
RC of facility* is X x pfx + Y x pfy MW
Where pf = required power factor:
Type A and B: ±0.95
Type C and D SPGM: ±0.92
Type C and D PPM: lozenge or bow tie as per G99 para 13.5.5
*note that there might be reactive compensation on site – which would need to be included appropriately in this calculation.
MEC is, say, 1.1(X+Y).
MIC is, say, 0.05(X+Y)
Y
X/2
X/2
MIC/ MEC at PoC

## Slide 29: PPM, SPGM and load
Power Generating Module (PGM)
Power Generating Facility (PGF)
PPM capacity is X MVA (ie 2 x X/2 MVA)
SGPM capacity is Y MVA
Load is 1.1Y (say)
RC of PPM is X x pfx MW
RC of SPGM is Y x pfy MW
RC of facility* is X x pfx + Y x pfy MW
Where pf = required power factor:
Type A and B: ±0.95
Type C and D SWPGM: ±0.92
Type C and D PPM: lozenge or bow tie as per G99 para 13.5.5
*note that there might be reactive compensation on site – which would need to be included appropriately in this calculation.
MEC could be X+Y
or MEC might typically be 1.1X
or could be X-0.1Y or 0.1Y or 0
MIC could be 1.1Y
or MIC might typically be 0.1Y
or MIC might be zero, or very close to.
Y
X/2
X/2
1.1Y
MIC/ MEC at PoC
As previous slide, but with site demand

## Slide 30: PPM and storage
Power Generating Module (PGM)
Power Generating Facility (PGF)
PPM capacity is X + Z MVA
RC of PPM is (X + Z) x pf MW
RCZ of facility* is (X + Z) x pfZ MW
Where pf = required power factor:
Type A and B: ±0.95
Type C and D synchronous: ±0.92
Type C and D PPM: lozenge or bow tie as per G99 para 13.5.5
*note that there might be reactive compensation on site – which would need to be included appropriately in this calculation.
MEC could be X+Z
MIC is probably Z (but could be a lot less)
Z
X/2
X/2
MIC/ MEC at PoC
As first example, but with storage forming part of the PPM

## Slide 31: PPM and storage; PGM output limited
Power Generating Module (PGM)
Power Generating Facility (PGF)
PPM capacity is X + Z MVA
RC of PPM is E x pf MW
RC of facility* is E x pf MW
Where pf = required power factor:
Type A and B: ±0.95
Type C and D SPGM: ±0.92
Type C and D PPM: lozenge or bow tie as per G99 para 13.5.5
*note that there might be reactive compensation on site – which would need to be included appropriately in this calculation.
† E could be any value less than X+Z, but likely that X ≤ E ≤ X+Z
Compliance based on RC – but note that it might need to be demonstrated for various mixes of generating units within the PPM.
MEC is E MVA
MIC is Z (but could be a lot less)
This approach is comparable with the intrinsic design capacity concept being considered for the fast track process.
Z
X/2
X/2
MIC/ MEC at PoC
PPM export limitation, eg overload relay, set at E†
As previous slide, but with the PPM output restricted

## Slide 32: PPM and storage; PGF export limited
Power Generating Module (PGM)
Power Generating Facility (PGF)
PPM capacity is X + Z MVA
RC of PPM is (X+Z) x pf MW
RC of facility* is (X+Z) x pf MW
Where pf = required power factor:
Type A and B: ±0.95
Type C and D synchronous: ±0.92
Type C and D PPM: lozenge or bow tie as per G99 para 13.5.5
*note that there might be reactive compensation on site – which would need to be included appropriately in this calculation.
† E could be any value less than X+Z, but likely that X ≤ E ≤ X+Z
PGM Compliance based on PGM’s RC – but note that it might need to be demonstrated for various mixes of generating units within the PPM.
MEC is E MVA
MIC is Z (but could be a lot less)
Z
X/2
X/2
MIC/ MEC at PoC
G100 Export Limitation System set at E†
As previous slide, but with site export restricted

## Slide 33: PPM, demand and storage; PGF export limited
Power Generating Module (PGM)
Power Generating Facility (PGF)
PPM capacity is X + Z MVA
RC of PPM is (X+Z) x pf MW
RC of facility* is (X+Z) x pf MW
Where pf = required power factor:
Type A and B: ±0.95
Type C and D SPGM: ±0.92
Type C and D PPM: lozenge or bow tie as per G99 para 13.5.5
*note that there might be reactive compensation on site – which would need to be included appropriately in this calculation.
† F could be any value less than X+Z, but likely that X-1.1Y ≤ F ≤ X+Z
G could any value up to 1.1Y + Z but likely to be G ≤ 0.6Y + Z or just G ≤ 0.6Y
.
MEC is F MVA
MIC is G MVA
Z
X/2
X/2
MIC/ MEC at PoC
G100 Limitation System set at F export, G import†
1.1Y
0.5Y
controllable load
As previous slide, but with site demand

## Slide 34: Outstanding Issues - 4.
No | Issue | Draft response
117 | Need of Effective date: Even though the current amendment is classified as minor changes there are significant changes that would require time for manufacturers to update their PGMs to comply with recent requirements. Ex one of those is the Cyber security requirement. For changes like these that would require identifying and implement a solution to an already compliant machine would take significant time/cost. Hence any requirements that would require modification of existing hardware/software design would require an effective date from the current release (a minimum of 6 months is recommended) to enable the manufacturer to be compliant with up-to-date requirements. Currently, the exception is applicable only for certain technologies but is required to be made for all technologies. Please be mindful that it would take manufacturers some time to find an effective solution and to prove compliance. | We agree that any change of requirements will generally need a period before compliance is required to allow manufacturers and others to accommodate the new requirements. As you are probably aware the recent modification to introduce new requirements for storage built in a 12 month period for manufactures and developers to implement any required changes before compliance is required. It might be that this is what you have in mind when you refer to the exception in your last sentence? We do not believe that there are any changes that we have classified as minor in the most recent amendment that impose any new compliance requirements on manufacturers or developers. Even without a specific formal implementation period, manufacturers do have significant warning of even the minor changes. They are all discussed at the DER Technical Forum, often over more than one meeting, and are summarised in the slides for the Forum which are published. The changes are formally consulted on, providing both an opportunity to absorb the proposed changes, to assimilate the implications, and provide a response or challenge to the proposals. There is then a further period, usually a couple of months, before the modification is approved by the regulator and published. In regard of the new references for cybersecurity, there is no new specific performance or compliance requirements added at this time, simply an expectation that manufacturers will be applying industry good practices, as well as standards that manufacturers should already be working to, or adapting to. It might be that the requirements of the network licensees, as provider of critical national infrastructure, do become more specific in the future, but we recognize this is a developing area and we are initially seeking to apply guidance and a light touch. In conjunction with BEIS ENA has produced guidance for Distributed energy resources (DER) cyber security connection at https://www.energynetworks.org/operating-the-networks/managing-cyber-security. However we do note your concern over the most recent change and we will be happy to discuss any points relating to them, or modifications to ENA documents more generally.

## Slide 35: Outstanding Issues – 5.
No | Issue | Draft response
118 | Clarification required on certificate/compliance validity: As it is difficult in managing different requirements at Plant level/PGMs/DNO/manufacturers it is requested to define the duration for the validity of a compliance report/certificate already obtained. | Our current working assumption is that any certification is valid for the working life of the equipment it is associated with, provided that (i) the manufacturer does not change the design or manufacturing techniques such that the original compliance assessment becomes invalid or (ii) the requirements in the Distribution Code (or G99 etc) do not change. In this case we would expect to draw explicit attention to this, as we have for the changes to the requirements for storage. Please note that 2.14 in G99 tries to make it clear that an update to G99 does not require any equipment to be recertified, unless the requirements have fundamentally changed.

## Slide 36: Outstanding Issues – 6.
No | Issue | Draft response
119 | Clarity on how the regulation is applied between releases: Manufacturers normally produce products in mass and it is difficult to keep the products up to date with frequently changing requirements and it is difficult to produce products to suit different regulatory releases either. Moreover, the Stock that would is currently held would be dead. Suppose a plant connection agreement is signed up for Amendment 4 and during the Connection phase and Amendment 8 is released, it would be difficult for manufacturers to produce products to be compliant with both 8 and 4. Similar confusion might arise for DNO while trying to maintain records of what Amendment applies to which plant/product during the FON stage. It is proposed that a similar method for expiry date is adopted from Germany. For example, if a product is certified in 2021 for Amendment 8, then it would be valid for 5 years. During the expiry of the certificate, the product has to be updated to the most recently released version. By doing so, it would be easy to manage the certificates from the Manufacturer side and DNO. | As stated in 117 and 118 above G99 does not require that changes to the drafting of G99 necessarily trigger a need for manufacturers to change anything (unless there has been a misapprehension of the existing requirements). Where there is a need to change equipment, and where there is stock in the supply chain, we would expect to provide sufficient time for manufacturers to be aware and to work the stock through the chain. This is why we provided a 12 month implementation period for the recent changes of requirements for storage. The Requirements for Generators formally provided a mechanism for plant in construction under a contract struck before the implementation date of the RfG could retain the pre-RfG requirements. This seems equitable and sensible and therefore it might be worth drafting an approach based on this principle into G99. Thank you for the suggestion re certification in terms of the German approach. We believe it introduces an automatically driven new workload for manufacturers, and in many cases would add little given the approach outlined in the above answers.

## Slide 37: Outstanding Issues – 7.
No | Issue | Draft response
120 | Regulated releases dates and updates to G99 It is recommended that G99 changes happen Annually or every 3 or 5 years similar to other regions in Europe. In the future, we would like to understand if there would be sudden releases similar to Amendment 7 and Amendment 8? If so, can it be avoided and change made annually or few years in once as there might be a difficulty for the users to keep up with the changes? Similar to Italy, is it possible just to release the version with details of what the new changes are instead of a complete release of an existing standard. This would be easier for DNO/Supplier/User to understand what is new between the baseline version and new amendments. The current version has changes in the revision table which is not covered in the document hence it is confusing. | 2021 was an exceptional year where we issued a number of versions which dealt with both legal and minor technical issues or provided clarification of clauses. We are very aware of the frequency of G99 amendments, and we also would like to restrict them to about one per year. G99 is subtly different to a conventional technical standard. It actually implements legal obligations that generation owners (and DNOs) have to meet. If a problem with its interpretation or implementation is brought to our attention, generally we need to deal with it expediently; otherwise the legal interpretation of the requirements might be misaligned with the actual requirements – and this can have an effect on developers who have projects in development that might being adversely affected by the text that needs modifying. G99 implemented a significant change in the requirements for generation in GB and took effect just over two years ago. Initially there were many queries raised, but the amendments made to date have generally now addressed most of these and we expect the pace of necessary changes to reduce. As regards understand the changes, the consultation version of the documents include full tracked changes, and the consultation paper explains each change and its relevance. However it might be helpful for us to publish as final change tracked version of the latest issue alongside the approved new version. This would provide a simple check for users as to what has changed from the text they are familiar with. We are currently exploring the option of publishing a track-changed version of the new documents alongside the Report to Authority documents on the Distribution Code website (http://www.dcode.org.uk/).

## Slide 38: Outstanding Issues – 8.
No | Issue | Draft response
121 | Minor corrections in G99 It is proposed to replace all "electricity storage devices" with "Energy storage devices". Currently, all the devices store the electricity in alternative energy form not as electric/charge form directly. Clarification on which requirements apply for Energy storage devices. As the word is included in synchronous machine and power pack modules. Synchronous machine working is limited by the machine's ability to fulfill grid codes, but convertor-based devices can be altered to fulfill stringent requirements due to electronic capability. Hence for devices that employing different technologies, it is recommended to keep the requirements separately and not to mix them. Clarity on what is the acceptable minimum level of cyber security required at the power generating module. Is it required for the power gen and the power generating control system components to be at the same security level as the facility and the ENA network? | G99 is a network oriented documented and as such it is blind to the storage medium. From the network perspective storage consumes electricity when charging, and produces electricity when discharging – ie a flow of electricity in and out. Energy storage includes heat storage, and electric vehicles, where the final output is heat and mechanical energy respectively, not electricity. The wording of the synchronous power generating module has been chosen deliberately to cater for technologies such as compressed air storage where the same synchronous machine is used for compression and expansion. In all cases the power generating module has to meet all the requirements for that technology, irrespective of how it is constituted. There are no specific requirements in G99 or G98 in relation to cybersecurity; only a general obligation to manage cyber risks appropriately.

## Slide 39: Outstanding Issues – 9.
No | Issue | Draft response
121 | Gas turbine can work independent of Heat recovery system and might start working before HR blocks starts. Hence recommended to show as two different modules instead of one. As once synchronized, it is possible for GT to run independently from the HR block. Modification of synchronous power generating module definition: recommend to remove energy storage device unless it is a flywheel like device that would be used as power generating device (ex. Mechanical UPS system - rotary UPS) but these devices are least used against grid as it supports power backup for short duration and just a load on grid until the grid fails. | Figure 4.1a shows a single power generating module comprising two separate power generating units. Whilst it is true that the gas turbine unit can be run independently, it is assumed that the steam turbine cannot. If the steam turbine were capable of independent operation then there would indeed be two separate synchronous PGMs. However as the steam turbine (a) cannot run independently and (b) normally runs in tandem with the gas turbine, the two units comprise a single SPGM. As per (a) above the definition caters for technologies such as hydro pumped storage and compressed air storage. Short term energy storage devices such as flywheels, DRUPs etc are specifically excluded from G99 – see section 7.1.2: “Equipment other than Generating Units (eg traction loads, lift motors etc) may act as a short term source of energy, and inject electrical energy into the Customer’s Installation when they operate in a regenerative mode. In general EREC G99 will not apply as there will be no need to make any specific design accommodation for such equipment as it is unlikely that they will support any possible power island for a significant length of time. Where such equipment can act as a source of electrical energy for more than a few seconds (say typically 20 s), the DNO will advise the Customer if the Customer’s Installation requires any special consideration such as reverse power protection on a case by case basis.”

## Slide 40: Update on G100 and Fast Track

## Slide 41: G100 and Fast Track
G100 WG - Last formal meeting 15 December and treatment of responses largely agreed.
There was also a meeting between BEAMA and some of the DNO reps on 25 January. This has resulted in some additional examples of application to loads being proposed in the current draft.
The next WG is 28 February when it is anticipated that the remaining changes and new material will be agreed and can then be presented to the DCRP – either for submission to Ofgem as a relevant Distribution Code document, or recommended for the ENA to publish outside of D Code governance.
DNOs are still reviewing fast track options, but hope to have proposals to take to the DCRP in April

## Slide 42: GC0117

## Slide 43: Grid Code Modification Proposal GC0117
Objective is to align the definition of Small and Large across GB.
Two key proposals being considered:
    Lower the Large threshold to 10MW in England and Wales
    Raise the 10MW and 30MW threshold in Scotland to 100MW
NGESO are arguing for the first of these options.
The effect would be that any generation ≥ 10MW would have to
  accede to the CUSC
  Be part of the Balancing Mechanism
  Provide data directly to NGESO
Consultation on the proposals is now expected middle of 2022

## Slide 44: GC0148 Emergency and Restoration

## Slide 45: Distributed Restart Project -1
Previous discussions on this topic have focussed on Distributed Restart. But there are no proposals that affect storage as well – see later.
Distributed Restart introduces the concept of an Anchor Generator, which is an embedded PGM cable of self starting and re-energising the DNO’s system, supplying DNO’s customers, and ideally being able to re-energize an element of the transmission system.
The Project’s working assumption is that such PGMs might be as small as 2MW. Initially NGESO assumed that all Anchor Generation would need to accede to the CUSC, but have now dropped that as an assumption – opening the opportunities to a wider population.
The draft requirements are being incorporated into Grid Code OC9 (black start) and OC5 (testing).
Matching requirements have been developed for the Distribution Code – which is particularly helpful if Anchor Generators (and other embedded Restoration Service Providers) are not CUSC parties.

## Slide 46: Distributed Restart Project - 2
G99 (and G59) largely avoids direct conflict with DRZ requirements, but would benefit from a few tweaks (particularly to the definition of its scope) to remove any possible confusion.
The project has completed draft amendments of the Grid Code, D Code, G59 and G99 which will form part of the formal consultations of GC0148.
NGESO have also introduced draft mandatory requirements on storage to have frequency response on falling frequency below statutory minimum, and a defined recovery response.
It has always been expected that these requirements on storage would be mirrored in G99 (and G98) in due course – although there is no need to match the GC0148 timescales.

## Slide 47: EU Developments

## Slide 48: EU developments
A new draft EU network code on cybersecurity was out for comment until 10 December.
There are three new expert groups starting that are likely to feed revisions into the EU Network Codes:
  Harmonization of certification and family groupings
  Advanced grid services and controls for grids with a high penetration of DER
  Connexion issues for offshore systems.
The third of these is unlikely to have any impact on DNOs and their stakeholders.

## Slide 49: Distribution Code Compliance

## Slide 50: Distribution Code Compliance
Background:
  The accelerated loss of mains programme requires that all generation in GB retrospectively adopts new loss of mains protection arrangements.
  In some cases these changes are not trivial.
  In some cases owners might ignore the requirements.
  DNOs have not had a strong historic need to rigorously enforce D Code compliance, and lack the legal tools and experience to routinely challenge non-compliances, both in general, but specifically for loss of mains protection.
Solution
  Modification DCRP/21/05/PC proposes D Code text that works through a managed compliance process over six months.
  Subject to appropriate checks and balances, if compliance not achieved in this timescale, the customer can be disconnected by the DNO.
  Following public consultation the DNOs submitted the modification to Ofgem for approval in early December and are now awaiting Ofgem’s decision.

## Slide 51: Wrap up:

## Slide 52: Minutes of previous meeting and actions
Outstanding matters arising not on the agenda:
  None?

## Slide 53: AOB and next meeting
AOB
None?
Next meeting?

## Slide 54
© ENA 2020