## Slide 1
DER Technical Forum
15 December 2022
09:00 – 11:00
Microsoft Teams meeting
Join on your computer, mobile app or room device
Click here to join the meeting
Meeting ID: 323 575 281 357 Passcode: akTPBr
Or call in (audio only)
+44 20 3855 5885,,585319406# United Kingdom, London
Phone Conference ID: 585 319 406#

## Slide 2: Welcome, Housekeeping and Introductions

## Slide 3: Agenda
1 | 09:00 | Welcome, Introductions and Acceptance of Agenda.
2 | 09:05 | Update on BESS issues
3 | 09:35 | New Issues since the last forum: none
4 | 09:40 | Unresolved issues 112, 113, 114, 117, 121-127
5 | 09:50 | Update on relevant topics: G100 Fastrack GC0117 Distributed Restart EU Developments
6 | 10:20 | AOB
7 | 10:30 | Next Meeting Arrangements

## Slide 4: Battery Energy Storage Systems

## Slide 5: BESS discussion session
A meeting was held with stakeholders on 29 November.
In light of some of the differences between DNOs’ approaches, further efforts are to be made to capture and compare the processes in detail.
It as also agreed by one DNO to take a lead in considering what blockers might exist to a more widespread use of voltage control (ie a voltage set point and slope) by BESSs.

## Slide 6: New Issues – None?

## Slide 7: Previous Issues

## Slide 8: Outstanding Issues:
Non-type-tested PGMs <16A – 125
Delays associated with DNOs being able to submit Mod Apps to NGESO because of inadequate SAF data – 126
Initial P28 assessments for generation tripping and/or load rejection etc. – 127
Older issues – included in the annex.
  Registered Capacity – 112
  BESS connexions – issues 113, 114
  Cybersecurity – 117 – to follow up with AMPS
  Classification of PGMs – 121 – to follow up with AMPS
  5 minutes per month for STP – 122

## Slide 9: Recent outstanding Issues – 1
No | Issue | Current Status
125 | Is it allowed to connect a non-type tested PGM where the registered capacity is <16A. There are some micro-hydro PGMs below the 16A threshold, but where they are designed to meet a specific location and as such are not amenable to type testing. | Although G99 was originally conceived as not allowing non-type-tested units of <16A to be connected, this could be overly restrictive in cases such as Nigel describes. It seems that the early drafting of 2.1 in G99 was designed to accommodate this – but it is less than completely clear and is in conflict with 2.4 DNOs have agreed that the drafting of 2.1 should be updated as shown below at the next opportunity. 2.1This EREC provides the technical requirements for the connection of Type A, Type B, Type C and Type D Power Generating Modules to the Distribution Networks of licensed DNOs in Great Britain. For the purposes of this EREC, a Power Generating Module is any source of electrical energy, irrespective of the generating technology and Power Generating Module type. This EREC applies to all Power Generating Modules which are not in the scope of EREC G98, Requirements for the connection of Fully Type Tested Micro-generators (up to and including 16 A per phase) in parallel with public Low Voltage Distribution Networks on or after 27 April 2019, or which would be in the scope of EREC G98 but are not suitable for type testing are not compatible with EREC G98. … 2.4 Specific separate requirements apply to Power Generating Facilities connected at LV comprising Fully Type Tested, Type A, Power Generating Modules 16 A/phase or less (micro-generators) and these are covered in EREC G98. All Power Generating Modules 16 A/phase or less connecting to the DNO’s Distribution Network shall be Fully Type Tested unless the DNO agrees that it is impractical where a Power Generating Module is being designed specifically for that location, such as is sometimes appropriate for micro hydro installations, etc.

## Slide 10: Recent outstanding Issues – 2
No | Issue | Current Status
126 | Customers are still seeing very long delays for DNOs to submit a Modification Application to National Grid for the appropriate GSP. A developer accepted a scheme Sept 2020 and only had the Mod App response back August 2022 (even with pushing for a Mod App to be done with escalation). This is not an isolated experience. One part of the delay occurred as the DNO informed us they are allowing customers to only fill in sections 1 -3 before receiving a distribution offer, but required customers to fill in section 4 before they were able to submit the Mod App. Whilst the customer UBGC represented had filled in Part 4 when the scheme was applied for, others which accepted before had not and a Mod App was further delayed, to allow customers who accepted ahead to fill in the form. This would have been 14+ months after they had initially accepted their offers. If Part 4 is a requirement for a Mod App but the DNO feels comfortable making a distribution offer without part 4, can it be agreed that part 4 it is filled in within a set period, I.e. 2-3 months of acceptance to prevent further delays in Modification Applications in the future or that the Mod App is submitted based only on the information within parts 1-3. | The timing of the provision of data is prescribed in DPC1 of the Distribution Code – needs review to see how this suggestion might be accommodated. Need to set up some discussions with appropriate DNO experts as soon as possible.

## Slide 11: Recent outstanding Issues – 3
No | Issue | Current Status
127 | There is a requirement in ENA P28/2 (Although fairly sketchily defined) that we are supposed to consider what happens if a generator trips under full load conditions at different power factors ie 0.95 lag, unity and 0.95 lead. We have had a fairly large number of these sites come up that have a problem on them, and when we carry out the studies, we get a fail (ie the SVC is greater than +/-3%). When we hit this point there isn’t really much we can do to help, as the SVC results are really just a function of the MW, MVAr flow and system strength – the only option is to constrain the generator MW output if it is at a problem PF – this causes headaches for developers Some general thoughts would be A generator tripping on full load conditions would be relatively unusual – although with G99 LoM protection I guess it can and does happen, so I can see why its there. Is it really realistic to consider it against minimum (outage) fault condition? Should the developer really be doing this and finding problems - it is such a simple assessment the DNO should really do this, and check before issuing an offer. In reality just a simple loadflow of before and after. | DNOs broadly agree that the DNO should undertake these checks early in the application process. It is appropriate (and necessary in P28) to consider outages. To be investigated further as part of the refinement of BESS processes.126.

## Slide 12: Update on G100 and Fast Track

## Slide 13: G100 & Fast track
Just a reminder from last meeting:
G100
  Issue 2 Amendment 1 has been published on 25 July.
  There are a small number of other points that stakeholders have commented on that would benefit from review at a suitable future time.
Fast track
  Ofgem has approved the modification on 09 September – effective from 09 November.

## Slide 14: GC0117

## Slide 15: GC0117 – alignment of Large, Medium and Small across GB
The WG consultation closed on 05 August:
  Out of 14 respondents, 3 support the original proposal (ie 10MW Large threshold throughout GB) and 3 support the WAGCM1 proposal (ie 100MW threshold). Some believed that the solutions had not been sufficiently fully developed. Others believe that a CBA and further investigations are required to fully assess the proposed solutions against the applicable Grid Code objectives.
  Some respondents expressed that the rationale / case for change is not clear. No demonstration of how the change would simplify and align Grid Code and generation considering discrepancies identified.
  Majority of respondents agreed that it is appropriate to change the definition of Demand Capacity and associated Grid Code definitions to align with the changes to Large, Medium and Small Power Stations but, via a separate modification.
  Most respondents were in support of revising the definition of Registered Capacity.
  Most respondents do not support a retrospective approach as it will be complex and result in increased costs.
  Majority supported establishing a holistic view of the required future net zero arrangements of the technical and commercial arrangements for connecting new and operating existing and new generators.
  A respondent advised that a holistic review is already being taken forward by the Open Networks project and continuing with GC0117 could result in duplication of effort and recommendations contrary to proposals under Open Networks.
This is being developed quite slowly, with the current activity focusing on NGESO creating a cost-benefit analysis (CBA). NGESO were only intending to cover NGESO costs and benefits, but Ofgem has advised that the costs and benefits for all affected parties must be included. It is not clear how NGESO will achieve this and they held a WG meeting about this on 08 December.
Further CBA meetings are scheduled for the new year.

## Slide 16: Distributed ReStart: GC0156 Electricity System Restoration Standard

## Slide 17: Electricity System Restoration Standard – GC0156
Distributed Restart is now being progressed as part of the wider ESRS implementation in GC0156
GC0156 formal working group consultation is open from 21 November to 29 December.
Matching D Code drafting is being consulted on from 12 December 2022 to 13 January 2023 – DCRP/22/02/PC: https://www.dcode.org.uk/consultations/open-consultations/
Interested DNO stakeholders should review the D Code drafting to ensure they understand the obligations on those who might wish to contract for Restoration Services.
NGESO also held a webinar re the proposals on 08/12.
https://www.nationalgrideso.com/electricity-transmission/document/272966/download

## Slide 18: EU Developments

## Slide 19: EU Update
All of this is not expected to have a direct effect on GB; however it will influence the wider market GB operates in.
ACER is now consulting on revisions to the RfG and DCC.
As expected, issues such as the inclusion of storage, and the revision of the Type D voltage threshold seem widely supported.
Including V2G is likely to be contentious. EU DSOs are playing a straight bat and treating EVs with and without V2G as RfG and DCC respectively. However the issue of AC coupled V2G has prompted the DSOs to state that AC coupled V2G can only be allowed via a properly installed charging point.

## Slide 20: RfG 2.0
ENTSO-e have made two proposals that could have far reaching implications for DNOs:
  RoCoF withstand is to be raised to 4Hz and that any LoM must not interfere with this. Not a problem for GB unless we decide (or are foreded) to adopt it – but a problem for Ireland.
  All B, C and D PPMs must be grid forming within three years of the entry into force. This will bring home some worries that grid forming PPMs:
    will be much more likely to form unintentional islands (and 4Hzs-1 RoCoF withstand will mean no RoCoF LoM )
    Do not have the same inherent damping as SGPMs, so multiple grid forming PPMs on distribution systems (with low X/R) will possibly oscillate unstably.
The consultation closed on 28/11. ACER will consult on their drafting proposals in Q2 2023 with likely transition into law in 2025.

## Slide 21: Other EU items
EN 50549-10 was published in the middle of November – although another review iteration is already supposed to have started in which case another version might appear in 12-18 months time.
The three current expert groups are getting to the reporting stage.
These may or may not feed into ACER’s work, dependent on timing:
  Harmonization of Certification and Produce Family Grouping
  Grids with a high penetration of PPMs
  Offshore grids

## Slide 22: Harmonization and Family Groupings
Deliver of this EG’s findings now expected in February. So far it looks like the report will cover the following:
Review of current EU practice
  Some interesting information, but very partial data and hard to draw conclusions
Simulation models for FRT
  Covering general guidance on parameters, settings, validation
  Black box models, and encryption
Harmonization of Type A Certificates
  Focus is on PGU, not on PGMs
  Defining common template which encompasses different member states’ requirements.
Harmonization of certificate acceptance
  Deals with both PGUs and PGMs
  Provides guidance on how certificates and schemes should be interpreted and accepted.
Family Definition
  Should cover approaches for SPGUs, wind PGUs; other converter PGUs.
  What must be held common, and what can vary within the family
  Applicability ranges
  Suitable evidence of family behaviour.

## Slide 23: Advanced capabilities for Grids with a high share of PPMs
This was not particularly pushed by ENTSO-e when the ESC was deciding what expert groups were necessary about a year ago.
In essence it seems to be a parallel exercise to the draft grid forming legal text which we know ENTSO-e has proposed to ACER as part of the consultation on amendments to the RfG.
It is too early to say how aligned these two approaches are, but it does seem that the expert group was leaning towards grid forming being a non-mandatory market led requirement (as per the current GB arrangements, rather than mandatory as being proposed by ENTSO-e.
ENTSO-e members are not particularly active in the EG; most of the work is being done by manufacturers.
Currently the report contains the Cenelec derived warnings about the possible stability impacts on DSO networks, as well as the risk of unintended islanding.
The report should be finished in March 2023.

## Slide 24: AOB and next meeting

## Slide 25: Appendix – historic Forum issues

## Slide 26: Outstanding Issues – 1
No | Issue | Assumed Status
112 | A common issue that keeps coming up is Registered Capacity vs design install and grid agreements. I have a specific case where the G99 and connection agreement is for 9MW, the developer undersized the inverters slightly. So it can only produce 8.5MW ( in round numbers) whilst operating in the 0.95 lag/lead range. This is what is shown when we do the G99 study, and we noted this shortfall. So the question arises, of what happens to the site now and what can it do. Specifically, 1) Is it’s new official RC 9MW or 8.5MW ie do they retain their original agreed capacity, or is this list back to the DNO? This is a common sticking point, taking the above example it cannot meet the 9MW required, but they may upgrade an inverter later to give them more MVAr headroom and it could then operate at 9MW. 2) If the DNO doesn’t want/need them to operate across the 0.95 lag/lead range can they then operate at 9MW active power and say unity or 0.98pf. In this case they are producing their official R, but their system design does not meet the required G99 standard for a 9MW site. | This is an issue that does re-appear from time to time. We have attempted to deal with it in the past in issues 40, 80 and 83. We went through it with slides at the 7 June 2022 DER TF. DNOs have summarized how they specify maximum capacities and power factors in their connexion agreements. We propose that we incorporate the material from the 7 June 2022 meeting into the next version of the DG guides

## Slide 27: Outstanding Issues – 2 – in progress
No | Issue | Assumed Status
113 | P28 has the usual classifications of frequent events, infrequent events (4 per month) and very infrequent events (1 per 3 month)…. what should we be assessing a storage system performing a dynamic containment service as? The UK grid is reasonably stable, at the moment, but with more conventional plant dropping out, the power swings are going to get a bit more sever, and the DC type services will be getting worked more often. Classing it as a very infrequent event probably isn’t realistic, but what about infrequent events? I could see that it is possible that you could get to around the 4 events per month, although probably not at the full power swing. | This is a good point, and one that probably would benefit from a consistent consideration by DNOs. It might be sensible to base the frequency on the observed incidence of frequency excursions, over the last 18 months say, that trigger a specific level of response from such services. The response level might be set locally, and the P28 “frequency of event” set by the historic track of frequency excursions triggering that level of response. This can be calculated from the information NGESO publish monthly. This should be picked up as part of ongoing work to develop a common approach to BESSs between the DNOs. However, note that in the BESS discussions on 18/11 it was pointed out that the 3% limit essentially applies at any time once the transients have died away, so for BESS power swings the 3% probably applies in all cases, irrespective of frequency of event.

## Slide 28: Outstanding Issues – 3 – in progress
No | Issue | Assumed Status
114 | We have concerns relating the voltage step change for Battery Energy Storage Systems (BESS) when the systems are designated for fast frequency response. A number of network operators define step change to be full declared export to full declared import for real power P and for reactive power Q. The FFR contracts do not have a contracted obligation to reverse the direction of reactive power flow and no obligation to match the fast MW response with a MVAr response. When importing, there is no obligation to operate at a particular power factor only to operate within a +/-0.95 range. If a full MW ramp has occurred, it is reasonable to assume the system is under stress. To reverse Q at this point would be the worst of all strategies at it would exacerbate the stress of the system by introducing an unnecessary voltage step. It is likely that EFR or FFR BESS is located at a point with a high X/R ratio (close to a BSP or GSP). Therefore a unit change in Q would have at least 10x the impact on at the voltage step that of a unit change in P. This Q reversal condition appears to be based on a false assumption about the default behaviour of inverters under FFR. We believe it is a matter for the customer to demonstrate through simulation the voltage step change under power reversal. It is a matter for the customer to produce a reactive power strategy that meets the constraints of the D Code and the connection offer. Confirmation of the simulation can be done via commissioning tests with frequency injection for smaller steps. The imposition of this requirement distorts the market by essentially limiting the capacity of a BESS scheme to around half the capacity of other technologies thus creating hidden barrier to the penetration of the technology. The customer should demonstrate how they meet the voltage step change challenge through modelling and if necessary to verify through commissioning demonstration, not for the network operator to impose a control philosophy. | To be picked up in the BESS sessions

## Slide 29: Outstanding Issues – 4 – in progress
No | Issue | Draft response
117 | Need of Effective date: Even though the current amendment is classified as minor changes there are significant changes that would require time for manufacturers to update their PGMs to comply with recent requirements. Ex one of those is the Cyber security requirement. For changes like these that would require identifying and implement a solution to an already compliant machine would take significant time/cost. Hence any requirements that would require modification of existing hardware/software design would require an effective date from the current release (a minimum of 6 months is recommended) to enable the manufacturer to be compliant with up-to-date requirements. Currently, the exception is applicable only for certain technologies but is required to be made for all technologies. Please be mindful that it would take manufacturers some time to find an effective solution and to prove compliance. | We agree that any change of requirements will generally need a period before compliance is required to allow manufacturers and others to accommodate the new requirements. As you are probably aware the recent modification to introduce new requirements for storage built in a 12 month period for manufactures and developers to implement any required changes before compliance is required. It might be that this is what you have in mind when you refer to the exception in your last sentence? We do not believe that there are any changes that we have classified as minor in the most recent amendment that impose any new compliance requirements on manufacturers or developers. Even without a specific formal implementation period, manufacturers do have significant warning of even the minor changes. They are all discussed at the DER Technical Forum, often over more than one meeting, and are summarised in the slides for the Forum which are published. The changes are formally consulted on, providing both an opportunity to absorb the proposed changes, to assimilate the implications, and provide a response or challenge to the proposals. There is then a further period, usually a couple of months, before the modification is approved by the regulator and published. In regard of the new references for cybersecurity, there is no new specific performance or compliance requirements added at this time, simply an expectation that manufacturers will be applying industry good practices, as well as standards that manufacturers should already be working to, or adapting to. It might be that the requirements of the network licensees, as provider of critical national infrastructure, do become more specific in the future, but we recognize this is a developing area and we are initially seeking to apply guidance and a light touch. In conjunction with BEIS ENA has produced guidance for Distributed energy resources (DER) cyber security connection at https://www.energynetworks.org/operating-the-networks/managing-cyber-security. However we do note your concern over the most recent change and we will be happy to discuss any points relating to them, or modifications to ENA documents more generally.

## Slide 30: Outstanding Issues – 5 – in progress
No | Issue | Draft response
121 | Minor corrections in G99 It is proposed to replace all "electricity storage devices" with "Energy storage devices". Currently, all the devices store the electricity in alternative energy form not as electric/charge form directly. Clarification on which requirements apply for Energy storage devices. As the word is included in synchronous machine and power pack modules. Synchronous machine working is limited by the machine's ability to fulfill grid codes, but convertor-based devices can be altered to fulfill stringent requirements due to electronic capability. Hence for devices that employing different technologies, it is recommended to keep the requirements separately and not to mix them. Clarity on what is the acceptable minimum level of cyber security required at the power generating module. Is it required for the power gen and the power generating control system components to be at the same security level as the facility and the ENA network? | G99 is a network oriented documented and as such it is blind to the storage medium. From the network perspective storage consumes electricity when charging, and produces electricity when discharging – ie a flow of electricity in and out. Energy storage includes heat storage, and electric vehicles, where the final output is heat and mechanical energy respectively, not electricity. The wording of the synchronous power generating module has been chosen deliberately to cater for technologies such as compressed air storage where the same synchronous machine is used for compression and expansion. In all cases the power generating module has to meet all the requirements for that technology, irrespective of how it is constituted. There are no specific requirements in G99 or G98 in relation to cybersecurity; only a general obligation to manage cyber risks appropriately.

## Slide 31: Outstanding Issues – 5 continued.
No | Issue | Draft response
121 | Gas turbine can work independent of Heat recovery system and might start working before HR blocks starts. Hence recommended to show as two different modules instead of one. As once synchronized, it is possible for GT to run independently from the HR block. Modification of synchronous power generating module definition: recommend to remove energy storage device unless it is a flywheel like device that would be used as power generating device (ex. Mechanical UPS system - rotary UPS) but these devices are least used against grid as it supports power backup for short duration and just a load on grid until the grid fails. | Figure 4.1a shows a single power generating module comprising two separate power generating units. Whilst it is true that the gas turbine unit can be run independently, it is assumed that the steam turbine cannot. If the steam turbine were capable of independent operation then there would indeed be two separate synchronous PGMs. However as the steam turbine (a) cannot run independently and (b) normally runs in tandem with the gas turbine, the two units comprise a single SPGM. As per (a) above the definition caters for technologies such as hydro pumped storage and compressed air storage. Short term energy storage devices such as flywheels, DRUPs etc are specifically excluded from G99 – see section 7.1.2: “Equipment other than Generating Units (eg traction loads, lift motors etc) may act as a short term source of energy, and inject electrical energy into the Customer’s Installation when they operate in a regenerative mode. In general EREC G99 will not apply as there will be no need to make any specific design accommodation for such equipment as it is unlikely that they will support any possible power island for a significant length of time. Where such equipment can act as a source of electrical energy for more than a few seconds (say typically 20 s), the DNO will advise the Customer if the Customer’s Installation requires any special consideration such as reverse power protection on a case by case basis.”

## Slide 32: Outstanding Issues – 7
No | Issue | Assumed Status
122 | I represent a UK water industry working group responsible for the development and maintenance of electrical specifications. During recent work to update a specification for low voltage diesel generator sets, I was asked by the group to lobby the ENA technical committee responsible for G99 to consider relaxing the following clause in EREC G99: 7.3.3.1 parallel operation | 7.3.3.1 The Power Generating Module may be permitted to operate in parallel with the Distribution Network for no more than 5 minutes in any month, and no more frequently than once per week. If the duration of parallel connection exceeds this period, or this frequency, then the Power Generating Module shall be considered as if it is, or can be, operated in long-term parallel operation mode. An alternative frequency and duration may be agreed between the DNO and the Generator taking account of particular site circumstances and Power Generating Module design. An electrical time interlock should be installed to ensure that the period of parallel operation does not exceed the agreed period. The timer should be a separate device from the changeover control system such that failure of the auto changeover system will not prevent the parallel being broken. Notice that the highlighted text already allows for an agreement between the DNO and Generator to agree an appropriate testing regime, subject to there being a valid reason to do so. An alternative would be to fit full LoM protection and address any relevant points from 7.3.3.4, in which case the PGM would be treated as LTP. To be reviewed as part of the next update to G99.

## Slide 33
© ENA 2020